## Sc 1
year | total_energy_requirement (MWh) | Energy Fulfilment Ratio (%) | Critical Load Interruptions | Estimated Loss due to Interruptions | Non-critical Load shedding events | Total Cost (M $) | Unit Cost ($/kWh) | Existing Solar PPA Total Energy Output (MWh) | Existing Solar PPA Total Cost of Operation (M $) | Existing Solar PPA Unit Cost ($/kWh) | PPA based on Solar plant source Total Energy Output (MWh) | PPA based on Solar plant source Total Cost of Operation (M $) | PPA based on Solar plant source Unit Cost ($/kWh) | PPA based on BESS Total Energy Output (MWh) | PPA based on BESS Total Cost of Operation (M $) | PPA based on BESS Unit Cost ($/kWh) | Captive DG Sets Total Energy Output (MWh) | Captive DG Sets Total Cost of Operation (M $) | Captive DG Sets Unit Cost ($/kWh)
1 | 42357.15 | 100 | 1 | 0.08 | 4 | 8.36 | 0.2 | 5571.09 | 0.21 | 0.04 | 31517.14 | 2.76 | 0.09 | 23220.32 | 4.08 | 0.18 | 4259.62 | 1.23 | 0.29
2 | 42357.15 | 100 | 0 | 0 | 5 | 8.28 | 0.2 | 5569.64 | 0.21 | 0.04 | 31575.19 | 2.76 | 0.09 | 23217.84 | 4.08 | 0.18 | 4273.46 | 1.23 | 0.29
3 | 45382.66 | 100 | 0 | 0 | 4 | 8.94 | 0.2 | 5585.42 | 0.21 | 0.04 | 34588.18 | 3.1 | 0.09 | 25051.48 | 4.42 | 0.18 | 4212.78 | 1.21 | 0.29
4 | 45382.66 | 100 | 0 | 0 | 4 | 8.93 | 0.2 | 5585.29 | 0.21 | 0.04 | 34547.15 | 3.1 | 0.09 | 25012.27 | 4.42 | 0.18 | 4193.67 | 1.2 | 0.29
5 | 49618.38 | 100 | 0 | 0 | 5 | 9.99 | 0.2 | 5548.18 | 0.21 | 0.04 | 38668.18 | 3.46 | 0.09 | 27740.17 | 5.1 | 0.18 | 4246.42 | 1.22 | 0.29
6 | 49618.38 | 100 | 0 | 0 | 6 | 9.99 | 0.2 | 5549.72 | 0.21 | 0.04 | 38602.28 | 3.46 | 0.09 | 27743.03 | 5.1 | 0.18 | 4258.21 | 1.22 | 0.29
7 | 49618.38 | 100 | 0 | 0 | 6 | 9.99 | 0.2 | 5548.18 | 0.21 | 0.04 | 38689.56 | 3.46 | 0.09 | 27706.75 | 5.1 | 0.18 | 4251.2 | 1.22 | 0.29
8 | 54459.19 | 100 | 0 | 0 | 4 | 11.13 | 0.2 | 5524.34 | 0.21 | 0.04 | 42962.25 | 3.82 | 0.09 | 30439.04 | 5.78 | 0.19 | 4681.34 | 1.32 | 0.28
9 | 54459.19 | 100 | 0 | 0 | 3 | 11.14 | 0.2 | 5525.56 | 0.21 | 0.04 | 42981.12 | 3.82 | 0.09 | 30425.78 | 5.78 | 0.19 | 4692.54 | 1.33 | 0.28
10 | 54459.19 | 100 | 0 | 0 | 3 | 11.78 | 0.22 | 5526.62 | 0.21 | 0.04 | 43107.54 | 3.82 | 0.09 | 30699.41 | 6.46 | 0.21 | 4529.67 | 1.29 | 0.28
11 | 57484.7 | 100 | 0 | 0 | 4 | 12.05 | 0.21 | 5602.35 | 0.21 | 0.04 | 45019.18 | 3.84 | 0.09 | 32142.47 | 6.46 | 0.2 | 5388.91 | 1.54 | 0.29
12 | 57484.7 | 100 | 0 | 0 | 4 | 12.05 | 0.21 | 5598.46 | 0.21 | 0.04 | 44960.09 | 3.84 | 0.09 | 32132.7 | 6.46 | 0.2 | 5416.38 | 1.54 | 0.28
| Existing Solar |  | 5 | MW
| Diesel Generator |  | 6 | No.
Solar PV PPA
|  |  | 40 | MW | from year 1
|  |  | 5 | MW | from year 3
|  |  | 5 | MW | from year 5
|  |  | 5 | MW | from year 8
BESS PPA
|  |  | 60 | MWh | from year 1
|  |  | 5 | MWh | from year 3
|  |  | 10 | MWh | from year 5
|  |  | 10 | MWh | from year 8
|  |  | 10 | MWh | from year 10

## Sc 1 Deck
Year | total_energy_requirement (MWh) | Energy Fulfilment Ratio (%) | Critical Load Interruptions | Estimated Loss due to Interruptions | Non-critical Load shedding events | Total Cost (M $) | Unit Cost ($/kWh) | Existing Solar PPA | Existing Solar PPA Total Cost of Operation (M $) | Existing Solar PPA Unit Cost ($/kWh) | PPA based on Solar plant source Total Energy Output (MWh) | PPA based on Solar plant source Total Cost of Operation (M $) | PPA based on Solar plant source Unit Cost ($/kWh) | PPA based on BESS Total Energy Output (MWh) | PPA based on BESS Total Cost of Operation (M $) | PPA based on BESS Unit Cost ($/kWh) | Captive DG Sets Total Energy Output (MWh) | Captive DG Sets Total Cost of Operation (M $) | Captive DG Sets Unit Cost ($/kWh) | Existing Solar PPA | New Solar PPA | Captive DG Sets | BESS PPA
1 | 42357.15 | 100 | 1 | 0.08 | 4 | 8.36 | 0.2 | 5571.09 | 0.21 | 0.04 | 31517.14 | 2.76 | 0.09 | 23220.32 | 4.08 | 0.18 | 4259.62 | 1.23 | 0.29 | 66.7349 | 467.2179 | 54.4042
2 | 42357.15 | 100 | 0 | 0 | 5 | 8.28 | 0.2 | 5569.64 | 0.21 | 0.04 | 31575.19 | 2.76 | 0.09 | 23217.84 | 4.08 | 0.18 | 4273.46 | 1.23 | 0.29 | 2.52 | 41.24 | 15.55 | 63.24
3 | 45382.66 | 100 | 0 | 0 | 4 | 8.94 | 0.2 | 5585.42 | 0.21 | 0.04 | 34588.18 | 3.1 | 0.09 | 25051.48 | 4.42 | 0.18 | 4212.78 | 1.21 | 0.29
4 | 45382.66 | 100 | 0 | 0 | 4 | 8.93 | 0.2 | 5585.29 | 0.21 | 0.04 | 34547.15 | 3.1 | 0.09 | 25012.27 | 4.42 | 0.18 | 4193.67 | 1.2 | 0.29
5 | 49618.38 | 100 | 0 | 0 | 5 | 9.99 | 0.2 | 5548.18 | 0.21 | 0.04 | 38668.18 | 3.46 | 0.09 | 27740.17 | 5.1 | 0.18 | 4246.42 | 1.22 | 0.29
6 | 49618.38 | 100 | 0 | 0 | 6 | 9.99 | 0.2 | 5549.72 | 0.21 | 0.04 | 38602.28 | 3.46 | 0.09 | 27743.03 | 5.1 | 0.18 | 4258.21 | 1.22 | 0.29
7 | 49618.38 | 100 | 0 | 0 | 6 | 9.99 | 0.2 | 5548.18 | 0.21 | 0.04 | 38689.56 | 3.46 | 0.09 | 27706.75 | 5.1 | 0.18 | 4251.2 | 1.22 | 0.29
8 | 54459.19 | 100 | 0 | 0 | 4 | 11.13 | 0.2 | 5524.34 | 0.21 | 0.04 | 42962.25 | 3.82 | 0.09 | 30439.04 | 5.78 | 0.19 | 4681.34 | 1.32 | 0.28
9 | 54459.19 | 100 | 0 | 0 | 3 | 11.14 | 0.2 | 5525.56 | 0.21 | 0.04 | 42981.12 | 3.82 | 0.09 | 30425.78 | 5.78 | 0.19 | 4692.54 | 1.33 | 0.28
10 | 54459.19 | 100 | 0 | 0 | 3 | 11.78 | 0.22 | 5526.62 | 0.21 | 0.04 | 43107.54 | 3.82 | 0.09 | 30699.41 | 6.46 | 0.21 | 4529.67 | 1.29 | 0.28
11 | 57484.7 | 100 | 0 | 0 | 4 | 12.05 | 0.21 | 5602.35 | 0.21 | 0.04 | 45019.18 | 3.84 | 0.09 | 32142.47 | 6.46 | 0.2 | 5388.91 | 1.54 | 0.29
12 | 57484.7 | 100 | 0 | 0 | 4 | 12.05 | 0.21 | 5598.46 | 0.21 | 0.04 | 44960.09 | 3.84 | 0.09 | 32132.7 | 6.46 | 0.2 | 5416.38 | 1.54 | 0.28

## Sc2
year | total_energy_requirement (MWh) | Energy Fulfilment Ratio (%) | Critical Load Interruptions | Estimated Loss due to Interruptions | Non-critical Load shedding events | Total Cost (M $) | Unit Cost ($/kWh) | Existing Solar PPA Total Energy Output (MWh) | Existing Solar PPA Total Cost of Operation (M $) | Existing Solar PPA Unit Cost ($/kWh) | PPA based on Solar plant source Total Energy Output (MWh) | PPA based on Solar plant source Total Cost of Operation (M $) | PPA based on Solar plant source Unit Cost ($/kWh) | PPA based on BESS Total Energy Output (MWh) | PPA based on BESS Total Cost of Operation (M $) | PPA based on BESS Unit Cost ($/kWh) | Captive DG Sets Total Energy Output (MWh) | Captive DG Sets Total Cost of Operation (M $) | Captive DG Sets Unit Cost ($/kWh)
1 | 42357.15 | 100 | 0 | 0 | 0 | 11.11 | 0.26 | 5444.48 | 0.21 | 0.04 | 33817.8 | 3.78 | 0.11 | 23913.13 | 6.46 | 0.27 | 2289.49 | 0.66 | 0.29
2 | 42357.15 | 100 | 0 | 0 | 0 | 11.11 | 0.26 | 5450.87 | 0.21 | 0.04 | 33805.22 | 3.78 | 0.11 | 23903.16 | 6.46 | 0.27 | 2273.07 | 0.66 | 0.29
3 | 45382.66 | 100 | 0 | 0 | 0 | 11.23 | 0.25 | 5499.88 | 0.21 | 0.04 | 36313.26 | 3.78 | 0.1 | 25758.5 | 6.46 | 0.25 | 2651.15 | 0.78 | 0.29
4 | 45382.66 | 100 | 0 | 0 | 0 | 11.23 | 0.25 | 5518.23 | 0.21 | 0.04 | 36296.77 | 3.78 | 0.1 | 25737.13 | 6.46 | 0.25 | 2640.84 | 0.78 | 0.3
5 | 49618.38 | 100 | 0 | 0 | 0 | 11.45 | 0.23 | 5520.68 | 0.21 | 0.04 | 39629.74 | 3.79 | 0.1 | 28244.15 | 6.46 | 0.23 | 3399.13 | 0.99 | 0.29
6 | 49618.38 | 100 | 0 | 0 | 0 | 11.45 | 0.23 | 5519.97 | 0.21 | 0.04 | 39627.88 | 3.79 | 0.1 | 28246.23 | 6.46 | 0.23 | 3398.16 | 0.99 | 0.29
7 | 49618.38 | 100 | 0 | 0 | 0 | 11.45 | 0.23 | 5510.66 | 0.21 | 0.04 | 39631.66 | 3.79 | 0.1 | 28225.81 | 6.46 | 0.23 | 3391.6 | 0.99 | 0.29
8 | 54459.19 | 100 | 0 | 0 | 3 | 11.78 | 0.22 | 5520.15 | 0.21 | 0.04 | 43081.38 | 3.82 | 0.09 | 30715.65 | 6.46 | 0.21 | 4530.24 | 1.29 | 0.28
9 | 54459.19 | 100 | 0 | 0 | 3 | 11.78 | 0.22 | 5524.81 | 0.21 | 0.04 | 43097.46 | 3.82 | 0.09 | 30711.44 | 6.46 | 0.21 | 4562.57 | 1.29 | 0.28
10 | 54459.19 | 100 | 0 | 0 | 3 | 11.78 | 0.22 | 5527.16 | 0.21 | 0.04 | 43105.47 | 3.82 | 0.09 | 30712.27 | 6.46 | 0.21 | 4537.49 | 1.29 | 0.28
11 | 57484.7 | 100 | 0 | 0 | 4 | 12.05 | 0.21 | 5596.43 | 0.21 | 0.04 | 44979.98 | 3.83 | 0.09 | 32117.75 | 6.46 | 0.2 | 5405.29 | 1.55 | 0.29
12 | 57484.7 | 100 | 0 | 0 | 3 | 12.05 | 0.21 | 5593.52 | 0.21 | 0.04 | 45010.47 | 3.84 | 0.09 | 32129.77 | 6.46 | 0.2 | 5410.16 | 1.54 | 0.28
| Existing Solar |  | 5 | MW
| Solar PV PPA |  | 55 | MW | from year 1
| BESS PPA |  | 95 | MWh | from year 1
| Diesel Generator |  | 6 | No.

## Sc 3
year | total_energy_requirement (MWh) | Energy Fulfilment Ratio (%) | Critical Load Interruptions | Estimated Loss due to Interruptions | Non-critical Load shedding events | Total Cost (M $) | Unit Cost ($/kWh) | Existing Solar PPA Total Energy Output (MWh) | Existing Solar PPA Total Cost of Operation (M $) | Existing Solar PPA Unit Cost ($/kWh) | PPA based on Solar plant source Total Energy Output (MWh) | PPA based on Solar plant source Total Cost of Operation (M $) | PPA based on Solar plant source Unit Cost ($/kWh) | PPA based on BESS Total Energy Output (MWh) | PPA based on BESS Total Cost of Operation (M $) | PPA based on BESS Unit Cost ($/kWh) | Captive DG Sets Total Energy Output (MWh) | Captive DG Sets Total Cost of Operation (M $) | Captive DG Sets Unit Cost ($/kWh)
1 | 42357.15 | 100 | 1 | 0.08 | 7 | 13.51 | 0.32 | 5777.26 | 0.22 | 0.04 | 26273.14 | 1.81 | 0.07 | 23932.1 | 8.97 | 0.37 | 8675.87 | 2.43 | 0.28
2 | 42357.15 | 100 | 1 | 0.08 | 10 | 13.51 | 0.32 | 5785.32 | 0.22 | 0.04 | 26315.25 | 1.82 | 0.07 | 23952.5 | 8.97 | 0.37 | 8664.67 | 2.42 | 0.28
3 | 45382.66 | 100 | 1 | 0.08 | 24 | 14.2 | 0.31 | 5820.98 | 0.22 | 0.04 | 27000.39 | 1.87 | 0.07 | 24704.91 | 8.97 | 0.36 | 10952.78 | 3.06 | 0.28
4 | 45382.66 | 100 | 1 | 0.08 | 20 | 14.19 | 0.31 | 5828.96 | 0.22 | 0.04 | 26961.26 | 1.86 | 0.07 | 24754.33 | 8.97 | 0.36 | 10965.51 | 3.06 | 0.28
5 | 49618.38 | 100 | 4 | 0.33 | 39 | 15.44 | 0.31 | 5836.37 | 0.22 | 0.04 | 27674.83 | 1.91 | 0.07 | 25265.91 | 8.97 | 0.36 | 14508.01 | 4.01 | 0.28
6 | 49618.38 | 99.99 | 2 | 0.17 | 42 | 15.31 | 0.31 | 5836.03 | 0.22 | 0.04 | 27669.55 | 1.91 | 0.07 | 25247.11 | 8.97 | 0.36 | 14571.72 | 4.04 | 0.28
7 | 49618.38 | 99.99 | 6 | 0.5 | 40 | 15.62 | 0.31 | 5827.86 | 0.22 | 0.04 | 27641.15 | 1.91 | 0.07 | 25223.98 | 8.97 | 0.36 | 14526.55 | 4.02 | 0.28
8 | 54459.19 | 99.93 | 11 | 0.91 | 57 | 17.3 | 0.32 | 5843.33 | 0.22 | 0.04 | 28068.48 | 1.92 | 0.07 | 24689.03 | 8.97 | 0.36 | 19115.05 | 5.28 | 0.28
9 | 54459.19 | 99.89 | 13 | 1.08 | 55 | 17.46 | 0.32 | 5836.73 | 0.22 | 0.04 | 28035.36 | 1.93 | 0.07 | 24615.67 | 8.97 | 0.36 | 19105.81 | 5.26 | 0.28
10 | 54459.19 | 99.92 | 9 | 0.74 | 62 | 17.14 | 0.31 | 5841.13 | 0.22 | 0.04 | 28071.41 | 1.94 | 0.07 | 24619.82 | 8.97 | 0.36 | 19108.71 | 5.27 | 0.28
11 | 57484.7 | 99.61 | 36 | 2.98 | 84 | 20.22 | 0.35 | 5850.33 | 0.22 | 0.04 | 28163.73 | 1.94 | 0.07 | 23663.4 | 8.97 | 0.38 | 22138.15 | 6.11 | 0.28
12 | 57484.7 | 99.54 | 43 | 3.56 | 82 | 20.79 | 0.36 | 5855.78 | 0.22 | 0.04 | 28181.02 | 1.94 | 0.07 | 23609.47 | 8.97 | 0.38 | 22109.25 | 6.1 | 0.28
| Existing Solar |  | 5 | MW
| Solar PV PPA |  | 35 | MW | from year 1
| BESS PPA |  | 130 | MWh | from year 1
| Diesel Generator |  | 6 | No.