## Slide 1: Alternative Power Strategy

## Slide 2: Background
SECMC is currently generating on diesel generator set with an average generation of 6 - 7 MW
Power generation cost from diesel is ~28 USc/kWh
The major load for power generation is dewatering pumps and CHS
To optimize the power generation cost, SECMC has explored various options which are presented in subsequent slides.
Background
Existing Power Scheme
14 MW HSD Engines
Existing 5MW Solar
  SECMC FOCUS
Cost Optimization
Reliability
Installation of additional Solar excluding already installed 5MW
Exploring the option of installing battery along with additional Solar for reliable operations and using curtailed renewable energy
Exploring other fuels in place of HSD, which are more commercially viable and readily available
Options Explored
Aux. power from Power Plant or grid connectivity to ensure reliable power supply

## Slide 3: Power Solution
  Solution – 2
  HSD + 10 MW Additional Solar + 6MW Battery
24-26 USc/kWh
Saving of 1 M USD/a
  Solution – 3
  10 MW Coal
10-13 USc/kWh
Saving of 7 M USD/a
  Solution – 1
  10 MW Rental RFO
18-20 USc/kWh
Saving of 4 M USD/a
Cheaper than the existing solution
Able to ramp accordingly with changing demand during operation
Lead time for Solar is ~9 months
  Pros
  Cons
High Renewable Contribution (~47%)
Able to ramp accordingly with changing demand during operation
  Cons
One of the cheapest options
Coal readily availability
  Cons
  Solution – 4
  Grid/Aux. Power from IPPs
18* USc/kWh
Saving of 5 M USD/a
Cheapest of all options
Grid power is consistent and stable.
More economical than independent power systems.
  Cons
  Pros
  Pros
  Pros
10 MW (rental)
5+10 MW
6 MW (existing HSD Gensets)
10 MW
More expensive than Coal
Low renewable contribution (~24%)
More expensive than Coal and RFO
Unreliable HSD supply given the current conditions
Unable to ramp with major load changes
High GHG emissions
Lead time for coal power plant is ~24 months
Grids can be susceptible to disruptions and load shedding
Energy transport over long distances can lead to losses.
5 MW
*The power tariff from the grid may reduce to 6 to 8 Usc/kWh in case of auxiliary power from IPPs
5 MW
Notes: RFO cost: 17.46 $/mmbtu, HSD cost: 28.00 $/mmbtu
5MW existing solar already incorporated in load profiling of SECMC
Existing Engine efficiency: 35%, RFO Engine Efficiency: 40%
RFO rental O&M cost: 5.86 USc/kWh
24 MW additional base load considered for expansion
The Capacity Factors are post curtailment on added energy
Coal power plant tariff: 9.5 Usc/kWh

## Slide 4: Comparison of Power Solutions
Financially Viable
Project Lead Time
Tariff
Potential Companies
Contract Duration
HFO Power Generation
18 to 20 USc/kWh
Lead time of around 6 to 9 months
Lower CAPEX & higher operating cost
Technomen Kinetics and Smart Power
10 MW (rental)
3 years on BOO Model
Short lead time but highest OPEX
Higher CAPEX & lower operating cost
Coal Power Plant
10 to 13 Usc/kWh
Lead time of around 2.5 to 3 years
Descon, Izhaar and Technomen kinetics, Etimaad
10 MW
Long term solution on BOO Model
Longest lead time and lowest OPEX, but will require an intermediate solution
Solar and Battery Storage System
Lead time of around 6 to 9 months
15 to 20 Usc/kWh
Higher CAPEX & lower operating cost
HUBCO, multiple vendors
10 MW Output
15 years on BOO Model
Shorter lead time and lower OPEX, though higher than coal