## Sheet1
MWh | M PKR |  |  | Grid MWh | PKR M
18169.9219 | 297.8301 | 342.6766 | 1530.2595 |  | 123.8482
18202.7999 | 487.5792 | 376.8352 | 1685.2014 |  | 146.95
16392.5944 | 314.6638 | 9.4458 | 38.5542 |  | 36.0604
16441.1458 | 335.049 | 18.9534 | 77.0466 |  | 42.9651
22887.3162 | 457.6003 | 26.5348 | 107.8652 |  | 50.1643
22935.8676 | 490.6387 | 0 | 0 |  | 44.0056
22984.419 | 524.1085 | 0 | 0 |  | 48.4061
23032.9704 | 562.796 | 13.2241 | 53.9759 |  | 60.0072

## scenario
Year | Solar Total Capacity MW | Solar Source Priority | BESS Total Capacity MW | BESS Source Priority | Gas Generator Total Capacity MW | Gas Generator Source Priority | Existing Gas Generators Total Capacity MW | Existing Gas Generators Source Priority | Grid Total Capacity MW | Grid Source Priority | Diesel Generator Total Capacity MW | Diesel Generator Source Priority
0 | 2 | 0 | 0 | 0 | 1.5 | 1 | 0 | 1 | 4.5 | 3 | 0 | 4
1 | 0 | 0 | 1.5 | 0 | 0 | 1 | 0 | 1 | 0 | 3 | 1.2 | 4
2 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 3 | 0 | 4
3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 3 | 0 | 4
4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 3 | 1.2 | 4
5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 3 | 0 | 4
6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 3 | 0 | 4
7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 3 | 0 | 4
8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 3 | 0 | 4

## power
year | month | hour | Prod Demand in MW | Cooling demand in TR | Free Cooling available in TR | BESS Charging Demand | Total power demand incl. Cooling & BESS in MW | Solar Output in MW | Solar Loading in % | Gas Generator Output in MW | Gas Generator Loading in % | Existing Gas Generators Output in MW | Existing Gas Generators Loading in % | Grid Output in MW | Grid Loading in % | Diesel Generator Output in MW | Diesel Generator Loading in % | Final Unserved Load
1 | 1 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 1 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 1 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 1 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 1 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 1 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 1 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 1 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.043648 | 100 | 1.4775 | 100 | 0 | 0 | 4.264 | 94.7561 | 0 | 0 | 0
1 | 1 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.47616 | 100 | 1.4775 | 100 | 0 | 0 | 3.8315 | 85.1447 | 0 | 0 | 0
1 | 1 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.87891 | 100 | 1.4775 | 100 | 0 | 0 | 3.4288 | 76.1947 | 0 | 0 | 0
1 | 1 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1825 | 100 | 1.4775 | 100 | 0 | 0 | 3.1252 | 69.4491 | 0 | 0 | 0
1 | 1 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3789 | 100 | 1.4775 | 100 | 0 | 0 | 2.9288 | 65.0843 | 0 | 0 | 0
1 | 1 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4523 | 100 | 1.4775 | 100 | 0 | 0 | 2.8554 | 63.453 | 0 | 0 | 0
1 | 1 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3967 | 100 | 1.4775 | 100 | 0 | 0 | 2.9109 | 64.6875 | 0 | 0 | 0
1 | 1 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.2241 | 100 | 1.4775 | 100 | 0 | 0 | 3.0835 | 68.5232 | 0 | 0 | 0
1 | 1 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.93446 | 100 | 1.4775 | 100 | 0 | 0 | 3.3732 | 74.9602 | 0 | 0 | 0
1 | 1 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.56346 | 100 | 1.4775 | 100 | 0 | 0 | 3.7442 | 83.2048 | 0 | 0 | 0
1 | 1 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.07936 | 100 | 1.4775 | 100 | 0 | 0 | 4.2283 | 93.9625 | 0 | 0 | 0
1 | 1 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 1 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 1 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 1 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 1 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 1 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 2 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 2 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 2 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 2 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 2 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 2 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 2 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 2 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.071424 | 100 | 1.4775 | 100 | 0 | 0 | 4.2362 | 94.1389 | 0 | 0 | 0
1 | 2 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.51981 | 100 | 1.4775 | 100 | 0 | 0 | 3.7879 | 84.1748 | 0 | 0 | 0
1 | 2 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.92256 | 100 | 1.4775 | 100 | 0 | 0 | 3.3851 | 75.2247 | 0 | 0 | 0
1 | 2 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.238 | 100 | 1.4775 | 100 | 0 | 0 | 3.0697 | 68.2146 | 0 | 0 | 0
1 | 2 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4503 | 100 | 1.4775 | 100 | 0 | 0 | 2.8574 | 63.4971 | 0 | 0 | 0
1 | 2 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.5336 | 100 | 1.4775 | 100 | 0 | 0 | 2.774 | 61.6454 | 0 | 0 | 0
1 | 2 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.494 | 100 | 1.4775 | 100 | 0 | 0 | 2.8137 | 62.5271 | 0 | 0 | 0
1 | 2 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3293 | 100 | 1.4775 | 100 | 0 | 0 | 2.9784 | 66.1865 | 0 | 0 | 0
1 | 2 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0555 | 100 | 1.4775 | 100 | 0 | 0 | 3.2522 | 72.2708 | 0 | 0 | 0
1 | 2 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.68845 | 100 | 1.4775 | 100 | 0 | 0 | 3.6192 | 80.4272 | 0 | 0 | 0
1 | 2 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.18054 | 100 | 1.4775 | 100 | 0 | 0 | 4.1271 | 91.714 | 0 | 0 | 0
1 | 2 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 2 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 2 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 2 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 2 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 2 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 3 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 3 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 3 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 3 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 3 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 3 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 3 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.001984 | 100 | 1.4775 | 100 | 0 | 0 | 4.3057 | 95.682 | 0 | 0 | 0
1 | 3 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.16467 | 100 | 1.4775 | 100 | 0 | 0 | 4.143 | 92.0667 | 0 | 0 | 0
1 | 3 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.59718 | 100 | 1.4775 | 100 | 0 | 0 | 3.7105 | 82.4553 | 0 | 0 | 0
1 | 3 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.98406 | 100 | 1.4775 | 100 | 0 | 0 | 3.3236 | 73.858 | 0 | 0 | 0
1 | 3 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.2737 | 100 | 1.4775 | 100 | 0 | 0 | 3.0339 | 67.421 | 0 | 0 | 0
1 | 3 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4741 | 100 | 1.4775 | 100 | 0 | 0 | 2.8336 | 62.968 | 0 | 0 | 0
1 | 3 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.5495 | 100 | 1.4775 | 100 | 0 | 0 | 2.7582 | 61.2927 | 0 | 0 | 0
1 | 3 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.5138 | 100 | 1.4775 | 100 | 0 | 0 | 2.7939 | 62.0863 | 0 | 0 | 0
1 | 3 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3114 | 100 | 1.4775 | 100 | 0 | 0 | 2.9962 | 66.5833 | 0 | 0 | 0
1 | 3 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0396 | 100 | 1.4775 | 100 | 0 | 0 | 3.2681 | 72.6235 | 0 | 0 | 0
1 | 3 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.68051 | 100 | 1.4775 | 100 | 0 | 0 | 3.6272 | 80.6036 | 0 | 0 | 0
1 | 3 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.25594 | 100 | 1.4775 | 100 | 0 | 0 | 4.0517 | 90.0386 | 0 | 0 | 0
1 | 3 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.001984 | 100 | 1.4775 | 100 | 0 | 0 | 4.3057 | 95.682 | 0 | 0 | 0
1 | 3 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 3 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 3 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 3 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 3 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 4 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 4 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 4 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 4 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 4 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 4 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 4 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.02976 | 100 | 1.4775 | 100 | 0 | 0 | 4.2779 | 95.0647 | 0 | 0 | 0
1 | 4 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.28768 | 100 | 1.4775 | 100 | 0 | 0 | 4.02 | 89.3332 | 0 | 0 | 0
1 | 4 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.66266 | 100 | 1.4775 | 100 | 0 | 0 | 3.645 | 81.0004 | 0 | 0 | 0
1 | 4 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0079 | 100 | 1.4775 | 100 | 0 | 0 | 3.2998 | 73.3289 | 0 | 0 | 0
1 | 4 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.2678 | 100 | 1.4775 | 100 | 0 | 0 | 3.0399 | 67.5533 | 0 | 0 | 0
1 | 4 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4265 | 100 | 1.4775 | 100 | 0 | 0 | 2.8812 | 64.0262 | 0 | 0 | 0
1 | 4 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4761 | 100 | 1.4775 | 100 | 0 | 0 | 2.8316 | 62.9239 | 0 | 0 | 0
1 | 4 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4027 | 100 | 1.4775 | 100 | 0 | 0 | 2.905 | 64.5552 | 0 | 0 | 0
1 | 4 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.2261 | 100 | 1.4775 | 100 | 0 | 0 | 3.0816 | 68.4791 | 0 | 0 | 0
1 | 4 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.95232 | 100 | 1.4775 | 100 | 0 | 0 | 3.3554 | 74.5634 | 0 | 0 | 0
1 | 4 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.62298 | 100 | 1.4775 | 100 | 0 | 0 | 3.6847 | 81.8822 | 0 | 0 | 0
1 | 4 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.26189 | 100 | 1.4775 | 100 | 0 | 0 | 4.0458 | 89.9063 | 0 | 0 | 0
1 | 4 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.01984 | 100 | 1.4775 | 100 | 0 | 0 | 4.2878 | 95.2852 | 0 | 0 | 0
1 | 4 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 4 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 4 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 4 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 4 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 5 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 5 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 5 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 5 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 5 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 5 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 5 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.071424 | 100 | 1.4775 | 100 | 0 | 0 | 4.2362 | 94.1389 | 0 | 0 | 0
1 | 5 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.31744 | 100 | 1.4775 | 100 | 0 | 0 | 3.9902 | 88.6719 | 0 | 0 | 0
1 | 5 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.64678 | 100 | 1.4775 | 100 | 0 | 0 | 3.6609 | 81.3531 | 0 | 0 | 0
1 | 5 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.95629 | 100 | 1.4775 | 100 | 0 | 0 | 3.3514 | 74.4752 | 0 | 0 | 0
1 | 5 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1904 | 100 | 1.4775 | 100 | 0 | 0 | 3.1173 | 69.2727 | 0 | 0 | 0
1 | 5 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3352 | 100 | 1.4775 | 100 | 0 | 0 | 2.9724 | 66.0543 | 0 | 0 | 0
1 | 5 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3749 | 100 | 1.4775 | 100 | 0 | 0 | 2.9328 | 65.1725 | 0 | 0 | 0
1 | 5 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3055 | 100 | 1.4775 | 100 | 0 | 0 | 3.0022 | 66.7156 | 0 | 0 | 0
1 | 5 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1388 | 100 | 1.4775 | 100 | 0 | 0 | 3.1689 | 70.4191 | 0 | 0 | 0
1 | 5 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.88685 | 100 | 1.4775 | 100 | 0 | 0 | 3.4208 | 76.0183 | 0 | 0 | 0
1 | 5 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.57536 | 100 | 1.4775 | 100 | 0 | 0 | 3.7323 | 82.9403 | 0 | 0 | 0
1 | 5 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.26586 | 100 | 1.4775 | 100 | 0 | 0 | 4.0418 | 89.8182 | 0 | 0 | 0
1 | 5 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.037696 | 100 | 1.4775 | 100 | 0 | 0 | 4.27 | 94.8884 | 0 | 0 | 0
1 | 5 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 5 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 5 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 5 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 5 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 6 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 6 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 6 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 6 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 6 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 6 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 6 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.06944 | 100 | 1.4775 | 100 | 0 | 0 | 4.2382 | 94.183 | 0 | 0 | 0
1 | 6 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.26189 | 100 | 1.4775 | 100 | 0 | 0 | 4.0458 | 89.9063 | 0 | 0 | 0
1 | 6 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.53766 | 100 | 1.4775 | 100 | 0 | 0 | 3.77 | 83.778 | 0 | 0 | 0
1 | 6 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.82138 | 100 | 1.4775 | 100 | 0 | 0 | 3.4863 | 77.4733 | 0 | 0 | 0
1 | 6 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0456 | 100 | 1.4775 | 100 | 0 | 0 | 3.2621 | 72.4912 | 0 | 0 | 0
1 | 6 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1805 | 100 | 1.4775 | 100 | 0 | 0 | 3.1272 | 69.4932 | 0 | 0 | 0
1 | 6 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.236 | 100 | 1.4775 | 100 | 0 | 0 | 3.0716 | 68.2587 | 0 | 0 | 0
1 | 6 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1785 | 100 | 1.4775 | 100 | 0 | 0 | 3.1292 | 69.5373 | 0 | 0 | 0
1 | 6 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0277 | 100 | 1.4775 | 100 | 0 | 0 | 3.28 | 72.888 | 0 | 0 | 0
1 | 6 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.81344 | 100 | 1.4775 | 100 | 0 | 0 | 3.4942 | 77.6496 | 0 | 0 | 0
1 | 6 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.54362 | 100 | 1.4775 | 100 | 0 | 0 | 3.7641 | 83.6457 | 0 | 0 | 0
1 | 6 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.26784 | 100 | 1.4775 | 100 | 0 | 0 | 4.0398 | 89.7741 | 0 | 0 | 0
1 | 6 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.055552 | 100 | 1.4775 | 100 | 0 | 0 | 4.2521 | 94.4916 | 0 | 0 | 0
1 | 6 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 6 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 6 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 6 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 6 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 7 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 7 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 7 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 7 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 7 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 7 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 7 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.037696 | 100 | 1.4775 | 100 | 0 | 0 | 4.27 | 94.8884 | 0 | 0 | 0
1 | 7 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.19443 | 100 | 1.4775 | 100 | 0 | 0 | 4.1132 | 91.4054 | 0 | 0 | 0
1 | 7 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.42259 | 100 | 1.4775 | 100 | 0 | 0 | 3.8851 | 86.3351 | 0 | 0 | 0
1 | 7 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.66861 | 100 | 1.4775 | 100 | 0 | 0 | 3.6391 | 80.8681 | 0 | 0 | 0
1 | 7 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.87494 | 100 | 1.4775 | 100 | 0 | 0 | 3.4327 | 76.2829 | 0 | 0 | 0
1 | 7 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0218 | 100 | 1.4775 | 100 | 0 | 0 | 3.2859 | 73.0203 | 0 | 0 | 0
1 | 7 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0753 | 100 | 1.4775 | 100 | 0 | 0 | 3.2323 | 71.8299 | 0 | 0 | 0
1 | 7 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0416 | 100 | 1.4775 | 100 | 0 | 0 | 3.2661 | 72.5794 | 0 | 0 | 0
1 | 7 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.92256 | 100 | 1.4775 | 100 | 0 | 0 | 3.3851 | 75.2247 | 0 | 0 | 0
1 | 7 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.71821 | 100 | 1.4775 | 100 | 0 | 0 | 3.5895 | 79.7659 | 0 | 0 | 0
1 | 7 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.48211 | 100 | 1.4775 | 100 | 0 | 0 | 3.8256 | 85.0125 | 0 | 0 | 0
1 | 7 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.24602 | 100 | 1.4775 | 100 | 0 | 0 | 4.0617 | 90.2591 | 0 | 0 | 0
1 | 7 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.057536 | 100 | 1.4775 | 100 | 0 | 0 | 4.2501 | 94.4475 | 0 | 0 | 0
1 | 7 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 7 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 7 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 7 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 7 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 8 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 8 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 8 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 8 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 8 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 8 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 8 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.021824 | 100 | 1.4775 | 100 | 0 | 0 | 4.2858 | 95.2411 | 0 | 0 | 0
1 | 8 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.20038 | 100 | 1.4775 | 100 | 0 | 0 | 4.1073 | 91.2731 | 0 | 0 | 0
1 | 8 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.46029 | 100 | 1.4775 | 100 | 0 | 0 | 3.8474 | 85.4975 | 0 | 0 | 0
1 | 8 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.72813 | 100 | 1.4775 | 100 | 0 | 0 | 3.5795 | 79.5455 | 0 | 0 | 0
1 | 8 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.95232 | 100 | 1.4775 | 100 | 0 | 0 | 3.3554 | 74.5634 | 0 | 0 | 0
1 | 8 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1051 | 100 | 1.4775 | 100 | 0 | 0 | 3.2026 | 71.1686 | 0 | 0 | 0
1 | 8 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1686 | 100 | 1.4775 | 100 | 0 | 0 | 3.1391 | 69.7577 | 0 | 0 | 0
1 | 8 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.113 | 100 | 1.4775 | 100 | 0 | 0 | 3.1946 | 70.9922 | 0 | 0 | 0
1 | 8 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.98208 | 100 | 1.4775 | 100 | 0 | 0 | 3.3256 | 73.9021 | 0 | 0 | 0
1 | 8 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.75987 | 100 | 1.4775 | 100 | 0 | 0 | 3.5478 | 78.84 | 0 | 0 | 0
1 | 8 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.496 | 100 | 1.4775 | 100 | 0 | 0 | 3.8117 | 84.7039 | 0 | 0 | 0
1 | 8 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.22816 | 100 | 1.4775 | 100 | 0 | 0 | 4.0795 | 90.6559 | 0 | 0 | 0
1 | 8 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.027776 | 100 | 1.4775 | 100 | 0 | 0 | 4.2799 | 95.1088 | 0 | 0 | 0
1 | 8 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 8 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 8 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 8 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 8 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 9 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 9 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 9 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 9 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 9 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 9 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 9 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.017856 | 100 | 1.4775 | 100 | 0 | 0 | 4.2898 | 95.3293 | 0 | 0 | 0
1 | 9 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.25792 | 100 | 1.4775 | 100 | 0 | 0 | 4.0498 | 89.9945 | 0 | 0 | 0
1 | 9 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.61504 | 100 | 1.4775 | 100 | 0 | 0 | 3.6926 | 82.0585 | 0 | 0 | 0
1 | 9 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.9424 | 100 | 1.4775 | 100 | 0 | 0 | 3.3653 | 74.7839 | 0 | 0 | 0
1 | 9 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1904 | 100 | 1.4775 | 100 | 0 | 0 | 3.1173 | 69.2727 | 0 | 0 | 0
1 | 9 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3452 | 100 | 1.4775 | 100 | 0 | 0 | 2.9625 | 65.8338 | 0 | 0 | 0
1 | 9 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3908 | 100 | 1.4775 | 100 | 0 | 0 | 2.9169 | 64.8198 | 0 | 0 | 0
1 | 9 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3114 | 100 | 1.4775 | 100 | 0 | 0 | 2.9962 | 66.5833 | 0 | 0 | 0
1 | 9 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.117 | 100 | 1.4775 | 100 | 0 | 0 | 3.1907 | 70.904 | 0 | 0 | 0
1 | 9 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.85709 | 100 | 1.4775 | 100 | 0 | 0 | 3.4506 | 76.6797 | 0 | 0 | 0
1 | 9 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.52378 | 100 | 1.4775 | 100 | 0 | 0 | 3.7839 | 84.0866 | 0 | 0 | 0
1 | 9 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.17062 | 100 | 1.4775 | 100 | 0 | 0 | 4.137 | 91.9344 | 0 | 0 | 0
1 | 9 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.001984 | 100 | 1.4775 | 100 | 0 | 0 | 4.3057 | 95.682 | 0 | 0 | 0
1 | 9 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 9 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 9 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 9 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 9 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 10 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 10 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 10 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 10 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 10 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 10 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 10 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 10 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.27181 | 100 | 1.4775 | 100 | 0 | 0 | 4.0359 | 89.6859 | 0 | 0 | 0
1 | 10 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.72614 | 100 | 1.4775 | 100 | 0 | 0 | 3.5815 | 79.5895 | 0 | 0 | 0
1 | 10 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0753 | 100 | 1.4775 | 100 | 0 | 0 | 3.2323 | 71.8299 | 0 | 0 | 0
1 | 10 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3273 | 100 | 1.4775 | 100 | 0 | 0 | 2.9804 | 66.2306 | 0 | 0 | 0
1 | 10 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4721 | 100 | 1.4775 | 100 | 0 | 0 | 2.8355 | 63.0121 | 0 | 0 | 0
1 | 10 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4959 | 100 | 1.4775 | 100 | 0 | 0 | 2.8117 | 62.4831 | 0 | 0 | 0
1 | 10 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3789 | 100 | 1.4775 | 100 | 0 | 0 | 2.9288 | 65.0843 | 0 | 0 | 0
1 | 10 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1567 | 100 | 1.4775 | 100 | 0 | 0 | 3.151 | 70.0223 | 0 | 0 | 0
1 | 10 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.84717 | 100 | 1.4775 | 100 | 0 | 0 | 3.4605 | 76.9001 | 0 | 0 | 0
1 | 10 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.47418 | 100 | 1.4775 | 100 | 0 | 0 | 3.8335 | 85.1888 | 0 | 0 | 0
1 | 10 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.061504 | 100 | 1.4775 | 100 | 0 | 0 | 4.2462 | 94.3593 | 0 | 0 | 0
1 | 10 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 10 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 10 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 10 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 10 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 10 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 11 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 11 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 11 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 11 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 11 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 11 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 11 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 11 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.1607 | 100 | 1.4775 | 100 | 0 | 0 | 4.147 | 92.1549 | 0 | 0 | 0
1 | 11 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.65274 | 100 | 1.4775 | 100 | 0 | 0 | 3.6549 | 81.2208 | 0 | 0 | 0
1 | 11 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0218 | 100 | 1.4775 | 100 | 0 | 0 | 3.2859 | 73.0203 | 0 | 0 | 0
1 | 11 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.2777 | 100 | 1.4775 | 100 | 0 | 0 | 3.03 | 67.3328 | 0 | 0 | 0
1 | 11 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4186 | 100 | 1.4775 | 100 | 0 | 0 | 2.8891 | 64.2025 | 0 | 0 | 0
1 | 11 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4324 | 100 | 1.4775 | 100 | 0 | 0 | 2.8752 | 63.8939 | 0 | 0 | 0
1 | 11 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3332 | 100 | 1.4775 | 100 | 0 | 0 | 2.9744 | 66.0983 | 0 | 0 | 0
1 | 11 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.111 | 100 | 1.4775 | 100 | 0 | 0 | 3.1966 | 71.0363 | 0 | 0 | 0
1 | 11 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.79757 | 100 | 1.4775 | 100 | 0 | 0 | 3.5101 | 78.0023 | 0 | 0 | 0
1 | 11 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.3472 | 100 | 1.4775 | 100 | 0 | 0 | 3.9605 | 88.0105 | 0 | 0 | 0
1 | 11 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 11 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 11 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 11 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 11 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 11 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 11 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 12 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 12 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 12 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 12 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 12 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 12 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 12 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 12 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.065472 | 100 | 1.4775 | 100 | 0 | 0 | 4.2422 | 94.2711 | 0 | 0 | 0
1 | 12 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.54163 | 100 | 1.4775 | 100 | 0 | 0 | 3.766 | 83.6898 | 0 | 0 | 0
1 | 12 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.92653 | 100 | 1.4775 | 100 | 0 | 0 | 3.3811 | 75.1366 | 0 | 0 | 0
1 | 12 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.2023 | 100 | 1.4775 | 100 | 0 | 0 | 3.1054 | 69.0082 | 0 | 0 | 0
1 | 12 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3709 | 100 | 1.4775 | 100 | 0 | 0 | 2.9367 | 65.2607 | 0 | 0 | 0
1 | 12 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4166 | 100 | 1.4775 | 100 | 0 | 0 | 2.8911 | 64.2466 | 0 | 0 | 0
1 | 12 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3313 | 100 | 1.4775 | 100 | 0 | 0 | 2.9764 | 66.1424 | 0 | 0 | 0
1 | 12 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1269 | 100 | 1.4775 | 100 | 0 | 0 | 3.1808 | 70.6836 | 0 | 0 | 0
1 | 12 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.8313 | 100 | 1.4775 | 100 | 0 | 0 | 3.4764 | 77.2528 | 0 | 0 | 0
1 | 12 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.38291 | 100 | 1.4775 | 100 | 0 | 0 | 3.9248 | 87.2169 | 0 | 0 | 0
1 | 12 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.003968 | 100 | 1.4775 | 100 | 0 | 0 | 4.3037 | 95.6379 | 0 | 0 | 0
1 | 12 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 12 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 12 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 12 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 12 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
1 | 12 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
2 | 1 | 1 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 1 | 2 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 1 | 3 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 1 | 4 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 1 | 5 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 1 | 6 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 1 | 7 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 1 | 8 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.043296 | 100 | 1.455 | 100 | 1.8 | 100 | 2.1594 | 47.9862 | 0 | 0 | 0
2 | 1 | 9 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.47232 | 100 | 1.455 | 100 | 1.8 | 100 | 1.7304 | 38.4523 | 0 | 0 | 0
2 | 1 | 10 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.87182 | 100 | 1.455 | 100 | 1.8 | 100 | 1.3308 | 29.5744 | 0 | 0 | 0
2 | 1 | 11 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.1729 | 100 | 1.455 | 100 | 1.8 | 100 | 1.0297 | 22.8832 | 0 | 0 | 0
2 | 1 | 12 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.3678 | 100 | 1.455 | 100 | 1.8 | 100 | 0.83491 | 18.5536 | 0 | 0 | 0
2 | 1 | 13 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.4406 | 100 | 1.455 | 100 | 1.8 | 100 | 0.7621 | 16.9355 | 0 | 0 | 0
2 | 1 | 14 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.3855 | 100 | 1.455 | 100 | 1.8 | 100 | 0.8172 | 18.16 | 0 | 0 | 0
2 | 1 | 15 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.2143 | 100 | 1.455 | 100 | 1.8 | 100 | 0.98842 | 21.9648 | 0 | 0 | 0
2 | 1 | 16 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.92693 | 100 | 1.455 | 100 | 1.8 | 100 | 1.2757 | 28.3499 | 0 | 0 | 0
2 | 1 | 17 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.55891 | 100 | 1.455 | 100 | 1.8 | 100 | 1.6438 | 36.528 | 0 | 0 | 0
2 | 1 | 18 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.07872 | 100 | 1.455 | 100 | 1.8 | 100 | 2.124 | 47.199 | 0 | 0 | 0
2 | 1 | 19 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 1 | 20 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 1 | 21 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 1 | 22 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 1 | 23 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 1 | 24 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 2 | 1 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 2 | 2 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 2 | 3 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 2 | 4 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 2 | 5 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 2 | 6 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 2 | 7 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 2 | 8 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.070848 | 100 | 1.455 | 100 | 1.8 | 100 | 2.1318 | 47.3739 | 0 | 0 | 0
2 | 2 | 9 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.51562 | 100 | 1.455 | 100 | 1.8 | 100 | 1.6871 | 37.4902 | 0 | 0 | 0
2 | 2 | 10 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.91512 | 100 | 1.455 | 100 | 1.8 | 100 | 1.2876 | 28.6123 | 0 | 0 | 0
2 | 2 | 11 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.228 | 100 | 1.455 | 100 | 1.8 | 100 | 0.97464 | 21.6587 | 0 | 0 | 0
2 | 2 | 12 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.4386 | 100 | 1.455 | 100 | 1.8 | 100 | 0.76406 | 16.9792 | 0 | 0 | 0
2 | 2 | 13 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.5213 | 100 | 1.455 | 100 | 1.8 | 100 | 0.68141 | 15.1424 | 0 | 0 | 0
2 | 2 | 14 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.4819 | 100 | 1.455 | 100 | 1.8 | 100 | 0.72077 | 16.0171 | 0 | 0 | 0
2 | 2 | 15 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.3186 | 100 | 1.455 | 100 | 1.8 | 100 | 0.88411 | 19.647 | 0 | 0 | 0
2 | 2 | 16 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.047 | 100 | 1.455 | 100 | 1.8 | 100 | 1.1557 | 25.6822 | 0 | 0 | 0
2 | 2 | 17 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.6829 | 100 | 1.455 | 100 | 1.8 | 100 | 1.5198 | 33.7728 | 0 | 0 | 0
2 | 2 | 18 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.17909 | 100 | 1.455 | 100 | 1.8 | 100 | 2.0236 | 44.9686 | 0 | 0 | 0
2 | 2 | 19 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 2 | 20 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 2 | 21 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 2 | 22 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 2 | 23 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 2 | 24 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 3 | 1 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 3 | 2 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 3 | 3 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 3 | 4 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 3 | 5 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 3 | 6 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 3 | 7 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.001968 | 100 | 1.455 | 100 | 1.8 | 100 | 2.2007 | 48.9046 | 0 | 0 | 0
2 | 3 | 8 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.16334 | 100 | 1.455 | 100 | 1.8 | 100 | 2.0393 | 45.3184 | 0 | 0 | 0
2 | 3 | 9 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.59237 | 100 | 1.455 | 100 | 1.8 | 100 | 1.6103 | 35.7846 | 0 | 0 | 0
2 | 3 | 10 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.97613 | 100 | 1.455 | 100 | 1.8 | 100 | 1.2265 | 27.2566 | 0 | 0 | 0
2 | 3 | 11 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.2635 | 100 | 1.455 | 100 | 1.8 | 100 | 0.93922 | 20.8715 | 0 | 0 | 0
2 | 3 | 12 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.4622 | 100 | 1.455 | 100 | 1.8 | 100 | 0.74045 | 16.4544 | 0 | 0 | 0
2 | 3 | 13 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.537 | 100 | 1.455 | 100 | 1.8 | 100 | 0.66566 | 14.7926 | 0 | 0 | 0
2 | 3 | 14 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.5016 | 100 | 1.455 | 100 | 1.8 | 100 | 0.70109 | 15.5798 | 0 | 0 | 0
2 | 3 | 15 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.3008 | 100 | 1.455 | 100 | 1.8 | 100 | 0.90182 | 20.0406 | 0 | 0 | 0
2 | 3 | 16 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.0312 | 100 | 1.455 | 100 | 1.8 | 100 | 1.1714 | 26.032 | 0 | 0 | 0
2 | 3 | 17 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.67502 | 100 | 1.455 | 100 | 1.8 | 100 | 1.5276 | 33.9478 | 0 | 0 | 0
2 | 3 | 18 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.25387 | 100 | 1.455 | 100 | 1.8 | 100 | 1.9488 | 43.3067 | 0 | 0 | 0
2 | 3 | 19 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.001968 | 100 | 1.455 | 100 | 1.8 | 100 | 2.2007 | 48.9046 | 0 | 0 | 0
2 | 3 | 20 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 3 | 21 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 3 | 22 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 3 | 23 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 3 | 24 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 4 | 1 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 4 | 2 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 4 | 3 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 4 | 4 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 4 | 5 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 4 | 6 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 4 | 7 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.02952 | 100 | 1.455 | 100 | 1.8 | 100 | 2.1732 | 48.2923 | 0 | 0 | 0
2 | 4 | 8 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.28536 | 100 | 1.455 | 100 | 1.8 | 100 | 1.9173 | 42.607 | 0 | 0 | 0
2 | 4 | 9 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.65731 | 100 | 1.455 | 100 | 1.8 | 100 | 1.5454 | 34.3414 | 0 | 0 | 0
2 | 4 | 10 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.99974 | 100 | 1.455 | 100 | 1.8 | 100 | 1.2029 | 26.7318 | 0 | 0 | 0
2 | 4 | 11 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.2576 | 100 | 1.455 | 100 | 1.8 | 100 | 0.94512 | 21.0027 | 0 | 0 | 0
2 | 4 | 12 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.415 | 100 | 1.455 | 100 | 1.8 | 100 | 0.78768 | 17.504 | 0 | 0 | 0
2 | 4 | 13 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.4642 | 100 | 1.455 | 100 | 1.8 | 100 | 0.73848 | 16.4107 | 0 | 0 | 0
2 | 4 | 14 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.3914 | 100 | 1.455 | 100 | 1.8 | 100 | 0.8113 | 18.0288 | 0 | 0 | 0
2 | 4 | 15 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.2162 | 100 | 1.455 | 100 | 1.8 | 100 | 0.98645 | 21.9211 | 0 | 0 | 0
2 | 4 | 16 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.94464 | 100 | 1.455 | 100 | 1.8 | 100 | 1.258 | 27.9563 | 0 | 0 | 0
2 | 4 | 17 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.61795 | 100 | 1.455 | 100 | 1.8 | 100 | 1.5847 | 35.216 | 0 | 0 | 0
2 | 4 | 18 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.25978 | 100 | 1.455 | 100 | 1.8 | 100 | 1.9429 | 43.1755 | 0 | 0 | 0
2 | 4 | 19 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.01968 | 100 | 1.455 | 100 | 1.8 | 100 | 2.183 | 48.511 | 0 | 0 | 0
2 | 4 | 20 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 4 | 21 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 4 | 22 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 4 | 23 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 4 | 24 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 5 | 1 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 5 | 2 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 5 | 3 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 5 | 4 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 5 | 5 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 5 | 6 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 5 | 7 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.070848 | 100 | 1.455 | 100 | 1.8 | 100 | 2.1318 | 47.3739 | 0 | 0 | 0
2 | 5 | 8 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.31488 | 100 | 1.455 | 100 | 1.8 | 100 | 1.8878 | 41.951 | 0 | 0 | 0
2 | 5 | 9 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.64157 | 100 | 1.455 | 100 | 1.8 | 100 | 1.5611 | 34.6912 | 0 | 0 | 0
2 | 5 | 10 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.94858 | 100 | 1.455 | 100 | 1.8 | 100 | 1.2541 | 27.8688 | 0 | 0 | 0
2 | 5 | 11 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.1808 | 100 | 1.455 | 100 | 1.8 | 100 | 1.0219 | 22.7083 | 0 | 0 | 0
2 | 5 | 12 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.3245 | 100 | 1.455 | 100 | 1.8 | 100 | 0.87821 | 19.5158 | 0 | 0 | 0
2 | 5 | 13 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.3638 | 100 | 1.455 | 100 | 1.8 | 100 | 0.83885 | 18.6411 | 0 | 0 | 0
2 | 5 | 14 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.2949 | 100 | 1.455 | 100 | 1.8 | 100 | 0.90773 | 20.1718 | 0 | 0 | 0
2 | 5 | 15 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.1296 | 100 | 1.455 | 100 | 1.8 | 100 | 1.073 | 23.8454 | 0 | 0 | 0
2 | 5 | 16 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.8797 | 100 | 1.455 | 100 | 1.8 | 100 | 1.323 | 29.3995 | 0 | 0 | 0
2 | 5 | 17 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.57072 | 100 | 1.455 | 100 | 1.8 | 100 | 1.632 | 36.2656 | 0 | 0 | 0
2 | 5 | 18 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.26371 | 100 | 1.455 | 100 | 1.8 | 100 | 1.939 | 43.088 | 0 | 0 | 0
2 | 5 | 19 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.037392 | 100 | 1.455 | 100 | 1.8 | 100 | 2.1653 | 48.1174 | 0 | 0 | 0
2 | 5 | 20 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 5 | 21 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 5 | 22 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 5 | 23 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 5 | 24 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 6 | 1 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 6 | 2 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 6 | 3 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 6 | 4 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 6 | 5 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 6 | 6 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 6 | 7 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.06888 | 100 | 1.455 | 100 | 1.8 | 100 | 2.1338 | 47.4176 | 0 | 0 | 0
2 | 6 | 8 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.25978 | 100 | 1.455 | 100 | 1.8 | 100 | 1.9429 | 43.1755 | 0 | 0 | 0
2 | 6 | 9 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.53333 | 100 | 1.455 | 100 | 1.8 | 100 | 1.6693 | 37.0966 | 0 | 0 | 0
2 | 6 | 10 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.81475 | 100 | 1.455 | 100 | 1.8 | 100 | 1.3879 | 30.8427 | 0 | 0 | 0
2 | 6 | 11 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.0371 | 100 | 1.455 | 100 | 1.8 | 100 | 1.1655 | 25.9008 | 0 | 0 | 0
2 | 6 | 12 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.171 | 100 | 1.455 | 100 | 1.8 | 100 | 1.0317 | 22.927 | 0 | 0 | 0
2 | 6 | 13 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.2261 | 100 | 1.455 | 100 | 1.8 | 100 | 0.97661 | 21.7024 | 0 | 0 | 0
2 | 6 | 14 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.169 | 100 | 1.455 | 100 | 1.8 | 100 | 1.0337 | 22.9707 | 0 | 0 | 0
2 | 6 | 15 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.0194 | 100 | 1.455 | 100 | 1.8 | 100 | 1.1832 | 26.2944 | 0 | 0 | 0
2 | 6 | 16 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.80688 | 100 | 1.455 | 100 | 1.8 | 100 | 1.3958 | 31.0176 | 0 | 0 | 0
2 | 6 | 17 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.53923 | 100 | 1.455 | 100 | 1.8 | 100 | 1.6634 | 36.9654 | 0 | 0 | 0
2 | 6 | 18 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.26568 | 100 | 1.455 | 100 | 1.8 | 100 | 1.937 | 43.0443 | 0 | 0 | 0
2 | 6 | 19 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.055104 | 100 | 1.455 | 100 | 1.8 | 100 | 2.1476 | 47.7238 | 0 | 0 | 0
2 | 6 | 20 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 6 | 21 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 6 | 22 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 6 | 23 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 6 | 24 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 7 | 1 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 7 | 2 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 7 | 3 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 7 | 4 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 7 | 5 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 7 | 6 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 7 | 7 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.037392 | 100 | 1.455 | 100 | 1.8 | 100 | 2.1653 | 48.1174 | 0 | 0 | 0
2 | 7 | 8 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.19286 | 100 | 1.455 | 100 | 1.8 | 100 | 2.0098 | 44.6624 | 0 | 0 | 0
2 | 7 | 9 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.41918 | 100 | 1.455 | 100 | 1.8 | 100 | 1.7835 | 39.6331 | 0 | 0 | 0
2 | 7 | 10 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.66322 | 100 | 1.455 | 100 | 1.8 | 100 | 1.5395 | 34.2102 | 0 | 0 | 0
2 | 7 | 11 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.86789 | 100 | 1.455 | 100 | 1.8 | 100 | 1.3348 | 29.6619 | 0 | 0 | 0
2 | 7 | 12 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.0135 | 100 | 1.455 | 100 | 1.8 | 100 | 1.1892 | 26.4256 | 0 | 0 | 0
2 | 7 | 13 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.0667 | 100 | 1.455 | 100 | 1.8 | 100 | 1.136 | 25.2448 | 0 | 0 | 0
2 | 7 | 14 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.0332 | 100 | 1.455 | 100 | 1.8 | 100 | 1.1695 | 25.9883 | 0 | 0 | 0
2 | 7 | 15 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.91512 | 100 | 1.455 | 100 | 1.8 | 100 | 1.2876 | 28.6123 | 0 | 0 | 0
2 | 7 | 16 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.71242 | 100 | 1.455 | 100 | 1.8 | 100 | 1.4903 | 33.1168 | 0 | 0 | 0
2 | 7 | 17 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.47822 | 100 | 1.455 | 100 | 1.8 | 100 | 1.7244 | 38.3211 | 0 | 0 | 0
2 | 7 | 18 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.24403 | 100 | 1.455 | 100 | 1.8 | 100 | 1.9586 | 43.5254 | 0 | 0 | 0
2 | 7 | 19 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.057072 | 100 | 1.455 | 100 | 1.8 | 100 | 2.1456 | 47.68 | 0 | 0 | 0
2 | 7 | 20 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 7 | 21 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 7 | 22 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 7 | 23 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 7 | 24 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 8 | 1 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 8 | 2 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 8 | 3 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 8 | 4 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 8 | 5 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 8 | 6 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 8 | 7 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.021648 | 100 | 1.455 | 100 | 1.8 | 100 | 2.181 | 48.4672 | 0 | 0 | 0
2 | 8 | 8 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.19877 | 100 | 1.455 | 100 | 1.8 | 100 | 2.0039 | 44.5312 | 0 | 0 | 0
2 | 8 | 9 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.45658 | 100 | 1.455 | 100 | 1.8 | 100 | 1.7461 | 38.8022 | 0 | 0 | 0
2 | 8 | 10 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.72226 | 100 | 1.455 | 100 | 1.8 | 100 | 1.4804 | 32.8982 | 0 | 0 | 0
2 | 8 | 11 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.94464 | 100 | 1.455 | 100 | 1.8 | 100 | 1.258 | 27.9563 | 0 | 0 | 0
2 | 8 | 12 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.0962 | 100 | 1.455 | 100 | 1.8 | 100 | 1.1065 | 24.5888 | 0 | 0 | 0
2 | 8 | 13 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.1592 | 100 | 1.455 | 100 | 1.8 | 100 | 1.0435 | 23.1894 | 0 | 0 | 0
2 | 8 | 14 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.104 | 100 | 1.455 | 100 | 1.8 | 100 | 1.0986 | 24.4139 | 0 | 0 | 0
2 | 8 | 15 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.97416 | 100 | 1.455 | 100 | 1.8 | 100 | 1.2285 | 27.3003 | 0 | 0 | 0
2 | 8 | 16 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.75374 | 100 | 1.455 | 100 | 1.8 | 100 | 1.4489 | 32.1984 | 0 | 0 | 0
2 | 8 | 17 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.492 | 100 | 1.455 | 100 | 1.8 | 100 | 1.7107 | 38.015 | 0 | 0 | 0
2 | 8 | 18 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.22632 | 100 | 1.455 | 100 | 1.8 | 100 | 1.9764 | 43.919 | 0 | 0 | 0
2 | 8 | 19 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.027552 | 100 | 1.455 | 100 | 1.8 | 100 | 2.1751 | 48.336 | 0 | 0 | 0
2 | 8 | 20 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 8 | 21 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 8 | 22 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 8 | 23 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 8 | 24 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 9 | 1 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 9 | 2 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 9 | 3 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 9 | 4 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 9 | 5 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 9 | 6 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 9 | 7 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.017712 | 100 | 1.455 | 100 | 1.8 | 100 | 2.185 | 48.5547 | 0 | 0 | 0
2 | 9 | 8 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.25584 | 100 | 1.455 | 100 | 1.8 | 100 | 1.9468 | 43.263 | 0 | 0 | 0
2 | 9 | 9 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.61008 | 100 | 1.455 | 100 | 1.8 | 100 | 1.5926 | 35.391 | 0 | 0 | 0
2 | 9 | 10 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.9348 | 100 | 1.455 | 100 | 1.8 | 100 | 1.2679 | 28.175 | 0 | 0 | 0
2 | 9 | 11 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.1808 | 100 | 1.455 | 100 | 1.8 | 100 | 1.0219 | 22.7083 | 0 | 0 | 0
2 | 9 | 12 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.3343 | 100 | 1.455 | 100 | 1.8 | 100 | 0.86837 | 19.2971 | 0 | 0 | 0
2 | 9 | 13 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.3796 | 100 | 1.455 | 100 | 1.8 | 100 | 0.8231 | 18.2912 | 0 | 0 | 0
2 | 9 | 14 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.3008 | 100 | 1.455 | 100 | 1.8 | 100 | 0.90182 | 20.0406 | 0 | 0 | 0
2 | 9 | 15 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.108 | 100 | 1.455 | 100 | 1.8 | 100 | 1.0947 | 24.3264 | 0 | 0 | 0
2 | 9 | 16 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.85018 | 100 | 1.455 | 100 | 1.8 | 100 | 1.3525 | 30.0555 | 0 | 0 | 0
2 | 9 | 17 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.51955 | 100 | 1.455 | 100 | 1.8 | 100 | 1.6831 | 37.4027 | 0 | 0 | 0
2 | 9 | 18 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.16925 | 100 | 1.455 | 100 | 1.8 | 100 | 2.0334 | 45.1872 | 0 | 0 | 0
2 | 9 | 19 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.001968 | 100 | 1.455 | 100 | 1.8 | 100 | 2.2007 | 48.9046 | 0 | 0 | 0
2 | 9 | 20 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 9 | 21 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 9 | 22 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 9 | 23 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 9 | 24 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 10 | 1 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 10 | 2 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 10 | 3 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 10 | 4 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 10 | 5 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 10 | 6 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 10 | 7 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 10 | 8 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.26962 | 100 | 1.455 | 100 | 1.8 | 100 | 1.9331 | 42.9568 | 0 | 0 | 0
2 | 10 | 9 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.72029 | 100 | 1.455 | 100 | 1.8 | 100 | 1.4824 | 32.9419 | 0 | 0 | 0
2 | 10 | 10 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.0667 | 100 | 1.455 | 100 | 1.8 | 100 | 1.136 | 25.2448 | 0 | 0 | 0
2 | 10 | 11 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.3166 | 100 | 1.455 | 100 | 1.8 | 100 | 0.88608 | 19.6907 | 0 | 0 | 0
2 | 10 | 12 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.4603 | 100 | 1.455 | 100 | 1.8 | 100 | 0.74242 | 16.4982 | 0 | 0 | 0
2 | 10 | 13 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.4839 | 100 | 1.455 | 100 | 1.8 | 100 | 0.7188 | 15.9734 | 0 | 0 | 0
2 | 10 | 14 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.3678 | 100 | 1.455 | 100 | 1.8 | 100 | 0.83491 | 18.5536 | 0 | 0 | 0
2 | 10 | 15 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.1473 | 100 | 1.455 | 100 | 1.8 | 100 | 1.0553 | 23.4518 | 0 | 0 | 0
2 | 10 | 16 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.84034 | 100 | 1.455 | 100 | 1.8 | 100 | 1.3623 | 30.2742 | 0 | 0 | 0
2 | 10 | 17 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.47035 | 100 | 1.455 | 100 | 1.8 | 100 | 1.7323 | 38.496 | 0 | 0 | 0
2 | 10 | 18 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.061008 | 100 | 1.455 | 100 | 1.8 | 100 | 2.1417 | 47.5926 | 0 | 0 | 0
2 | 10 | 19 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 10 | 20 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 10 | 21 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 10 | 22 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 10 | 23 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 10 | 24 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 11 | 1 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 11 | 2 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 11 | 3 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 11 | 4 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 11 | 5 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 11 | 6 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 11 | 7 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 11 | 8 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.15941 | 100 | 1.455 | 100 | 1.8 | 100 | 2.0433 | 45.4059 | 0 | 0 | 0
2 | 11 | 9 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.64747 | 100 | 1.455 | 100 | 1.8 | 100 | 1.5552 | 34.56 | 0 | 0 | 0
2 | 11 | 10 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.0135 | 100 | 1.455 | 100 | 1.8 | 100 | 1.1892 | 26.4256 | 0 | 0 | 0
2 | 11 | 11 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.2674 | 100 | 1.455 | 100 | 1.8 | 100 | 0.93528 | 20.784 | 0 | 0 | 0
2 | 11 | 12 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.4071 | 100 | 1.455 | 100 | 1.8 | 100 | 0.79555 | 17.679 | 0 | 0 | 0
2 | 11 | 13 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.4209 | 100 | 1.455 | 100 | 1.8 | 100 | 0.78178 | 17.3728 | 0 | 0 | 0
2 | 11 | 14 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.3225 | 100 | 1.455 | 100 | 1.8 | 100 | 0.88018 | 19.5595 | 0 | 0 | 0
2 | 11 | 15 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.1021 | 100 | 1.455 | 100 | 1.8 | 100 | 1.1006 | 24.4576 | 0 | 0 | 0
2 | 11 | 16 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.79114 | 100 | 1.455 | 100 | 1.8 | 100 | 1.4115 | 31.3675 | 0 | 0 | 0
2 | 11 | 17 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.3444 | 100 | 1.455 | 100 | 1.8 | 100 | 1.8583 | 41.295 | 0 | 0 | 0
2 | 11 | 18 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 11 | 19 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 11 | 20 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 11 | 21 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 11 | 22 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 11 | 23 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 11 | 24 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 12 | 1 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 12 | 2 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 12 | 3 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 12 | 4 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 12 | 5 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 12 | 6 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 12 | 7 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 12 | 8 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.064944 | 100 | 1.455 | 100 | 1.8 | 100 | 2.1377 | 47.5051 | 0 | 0 | 0
2 | 12 | 9 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.53726 | 100 | 1.455 | 100 | 1.8 | 100 | 1.6654 | 37.0091 | 0 | 0 | 0
2 | 12 | 10 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.91906 | 100 | 1.455 | 100 | 1.8 | 100 | 1.2836 | 28.5248 | 0 | 0 | 0
2 | 12 | 11 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.1926 | 100 | 1.455 | 100 | 1.8 | 100 | 1.0101 | 22.4459 | 0 | 0 | 0
2 | 12 | 12 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.3599 | 100 | 1.455 | 100 | 1.8 | 100 | 0.84278 | 18.7286 | 0 | 0 | 0
2 | 12 | 13 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.4052 | 100 | 1.455 | 100 | 1.8 | 100 | 0.79752 | 17.7227 | 0 | 0 | 0
2 | 12 | 14 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.3205 | 100 | 1.455 | 100 | 1.8 | 100 | 0.88214 | 19.6032 | 0 | 0 | 0
2 | 12 | 15 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 1.1178 | 100 | 1.455 | 100 | 1.8 | 100 | 1.0848 | 24.1078 | 0 | 0 | 0
2 | 12 | 16 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.82459 | 100 | 1.455 | 100 | 1.8 | 100 | 1.3781 | 30.624 | 0 | 0 | 0
2 | 12 | 17 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.37982 | 100 | 1.455 | 100 | 1.8 | 100 | 1.8228 | 40.5078 | 0 | 0 | 0
2 | 12 | 18 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.003936 | 100 | 1.455 | 100 | 1.8 | 100 | 2.1987 | 48.8608 | 0 | 0 | 0
2 | 12 | 19 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 12 | 20 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 12 | 21 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 12 | 22 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 12 | 23 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
2 | 12 | 24 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0 | 0 | 1.455 | 100 | 1.8 | 100 | 2.2027 | 48.9483 | 0 | 0 | 0
3 | 1 | 1 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 1 | 2 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 1 | 3 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 1 | 4 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 1 | 5 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 1 | 6 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 1 | 7 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 1 | 8 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.042944 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.2183 | 49.2966 | 0 | 0 | 0
3 | 1 | 9 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.46848 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.7928 | 39.8403 | 0 | 0 | 0
3 | 1 | 10 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.86474 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.3966 | 31.0346 | 0 | 0 | 0
3 | 1 | 11 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.1634 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.0979 | 24.3978 | 0 | 0 | 0
3 | 1 | 12 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.3566 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.90465 | 20.1034 | 0 | 0 | 0
3 | 1 | 13 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.4289 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.83243 | 18.4984 | 0 | 0 | 0
3 | 1 | 14 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.3742 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.88709 | 19.713 | 0 | 0 | 0
3 | 1 | 15 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.2044 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.0569 | 23.4869 | 0 | 0 | 0
3 | 1 | 16 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.91939 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.3419 | 29.82 | 0 | 0 | 0
3 | 1 | 17 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.55437 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.7069 | 37.9317 | 0 | 0 | 0
3 | 1 | 18 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.07808 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.1832 | 48.5158 | 0 | 0 | 0
3 | 1 | 19 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 1 | 20 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 1 | 21 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 1 | 22 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 1 | 23 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 1 | 24 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 2 | 1 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 2 | 2 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 2 | 3 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 2 | 4 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 2 | 5 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 2 | 6 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 2 | 7 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 2 | 8 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.070272 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.191 | 48.6894 | 0 | 0 | 0
3 | 2 | 9 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.51142 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.7499 | 38.886 | 0 | 0 | 0
3 | 2 | 10 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.90768 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.3536 | 30.0803 | 0 | 0 | 0
3 | 2 | 11 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.218 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.0432 | 23.1832 | 0 | 0 | 0
3 | 2 | 12 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.4269 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.83438 | 18.5418 | 0 | 0 | 0
3 | 2 | 13 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.5089 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.7524 | 16.7199 | 0 | 0 | 0
3 | 2 | 14 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.4699 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.79144 | 17.5875 | 0 | 0 | 0
3 | 2 | 15 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.3078 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.95345 | 21.1878 | 0 | 0 | 0
3 | 2 | 16 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.0385 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.2228 | 27.174 | 0 | 0 | 0
3 | 2 | 17 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.67734 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.5839 | 35.1989 | 0 | 0 | 0
3 | 2 | 18 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.17763 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.0837 | 46.3036 | 0 | 0 | 0
3 | 2 | 19 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 2 | 20 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 2 | 21 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 2 | 22 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 2 | 23 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 2 | 24 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 3 | 1 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 3 | 2 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 3 | 3 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 3 | 4 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 3 | 5 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 3 | 6 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 3 | 7 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.001952 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.2593 | 50.2076 | 0 | 0 | 0
3 | 3 | 8 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.16202 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.0993 | 46.6506 | 0 | 0 | 0
3 | 3 | 9 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.58755 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.6737 | 37.1942 | 0 | 0 | 0
3 | 3 | 10 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.96819 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.2931 | 28.7356 | 0 | 0 | 0
3 | 3 | 11 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.2532 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.0081 | 22.4024 | 0 | 0 | 0
3 | 3 | 12 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.4503 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.81096 | 18.0213 | 0 | 0 | 0
3 | 3 | 13 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.5245 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.73678 | 16.3729 | 0 | 0 | 0
3 | 3 | 14 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.4894 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.77192 | 17.1537 | 0 | 0 | 0
3 | 3 | 15 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.2903 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.97102 | 21.5782 | 0 | 0 | 0
3 | 3 | 16 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.0228 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.2384 | 27.521 | 0 | 0 | 0
3 | 3 | 17 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.66954 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.5918 | 35.3724 | 0 | 0 | 0
3 | 3 | 18 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.25181 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.0095 | 44.6552 | 0 | 0 | 0
3 | 3 | 19 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.001952 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.2593 | 50.2076 | 0 | 0 | 0
3 | 3 | 20 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 3 | 21 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 3 | 22 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 3 | 23 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 3 | 24 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 4 | 1 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 4 | 2 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 4 | 3 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 4 | 4 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 4 | 5 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 4 | 6 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 4 | 7 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.02928 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.232 | 49.6003 | 0 | 0 | 0
3 | 4 | 8 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.28304 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.9783 | 43.9612 | 0 | 0 | 0
3 | 4 | 9 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.65197 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.6093 | 35.7628 | 0 | 0 | 0
3 | 4 | 10 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.99162 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.2697 | 28.215 | 0 | 0 | 0
3 | 4 | 11 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.2473 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.014 | 22.5326 | 0 | 0 | 0
3 | 4 | 12 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.4035 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.85781 | 19.0623 | 0 | 0 | 0
3 | 4 | 13 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.4523 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.80901 | 17.9779 | 0 | 0 | 0
3 | 4 | 14 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.3801 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.88123 | 19.5829 | 0 | 0 | 0
3 | 4 | 15 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.2063 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.055 | 23.4435 | 0 | 0 | 0
3 | 4 | 16 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.93696 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.3243 | 29.4296 | 0 | 0 | 0
3 | 4 | 17 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.61293 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.6484 | 36.6303 | 0 | 0 | 0
3 | 4 | 18 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.25766 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.0036 | 44.5251 | 0 | 0 | 0
3 | 4 | 19 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.01952 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.2418 | 49.8172 | 0 | 0 | 0
3 | 4 | 20 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 4 | 21 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 4 | 22 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 4 | 23 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 4 | 24 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 5 | 1 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 5 | 2 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 5 | 3 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 5 | 4 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 5 | 5 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 5 | 6 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 5 | 7 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.070272 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.191 | 48.6894 | 0 | 0 | 0
3 | 5 | 8 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.31232 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.949 | 43.3105 | 0 | 0 | 0
3 | 5 | 9 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.63635 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.6249 | 36.1098 | 0 | 0 | 0
3 | 5 | 10 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.94086 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.3204 | 29.3429 | 0 | 0 | 0
3 | 5 | 11 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.1712 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.0901 | 24.2243 | 0 | 0 | 0
3 | 5 | 12 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.3137 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.9476 | 21.0577 | 0 | 0 | 0
3 | 5 | 13 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.3527 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.90856 | 20.1902 | 0 | 0 | 0
3 | 5 | 14 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.2844 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.97688 | 21.7084 | 0 | 0 | 0
3 | 5 | 15 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.1204 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.1408 | 25.3521 | 0 | 0 | 0
3 | 5 | 16 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.87254 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.3887 | 30.8611 | 0 | 0 | 0
3 | 5 | 17 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.56608 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.6952 | 37.6714 | 0 | 0 | 0
3 | 5 | 18 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.26157 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.9997 | 44.4383 | 0 | 0 | 0
3 | 5 | 19 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.037088 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.2242 | 49.4268 | 0 | 0 | 0
3 | 5 | 20 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 5 | 21 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 5 | 22 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 5 | 23 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 5 | 24 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 6 | 1 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 6 | 2 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 6 | 3 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 6 | 4 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 6 | 5 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 6 | 6 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 6 | 7 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.06832 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.193 | 48.7327 | 0 | 0 | 0
3 | 6 | 8 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.25766 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.0036 | 44.5251 | 0 | 0 | 0
3 | 6 | 9 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.52899 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.7323 | 38.4956 | 0 | 0 | 0
3 | 6 | 10 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.80813 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.4532 | 32.2926 | 0 | 0 | 0
3 | 6 | 11 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.0287 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.2326 | 27.3909 | 0 | 0 | 0
3 | 6 | 12 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.1614 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.0999 | 24.4412 | 0 | 0 | 0
3 | 6 | 13 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.2161 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.0452 | 23.2266 | 0 | 0 | 0
3 | 6 | 14 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.1595 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.1018 | 24.4846 | 0 | 0 | 0
3 | 6 | 15 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.0111 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.2502 | 27.7813 | 0 | 0 | 0
3 | 6 | 16 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.80032 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.461 | 32.4661 | 0 | 0 | 0
3 | 6 | 17 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.53485 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.7264 | 38.3654 | 0 | 0 | 0
3 | 6 | 18 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.26352 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.9978 | 44.395 | 0 | 0 | 0
3 | 6 | 19 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.054656 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.2066 | 49.0364 | 0 | 0 | 0
3 | 6 | 20 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 6 | 21 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 6 | 22 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 6 | 23 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 6 | 24 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 7 | 1 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 7 | 2 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 7 | 3 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 7 | 4 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 7 | 5 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 7 | 6 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 7 | 7 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.037088 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.2242 | 49.4268 | 0 | 0 | 0
3 | 7 | 8 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.1913 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.07 | 45.9999 | 0 | 0 | 0
3 | 7 | 9 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.41578 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.8455 | 41.0115 | 0 | 0 | 0
3 | 7 | 10 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.65782 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.6035 | 35.6326 | 0 | 0 | 0
3 | 7 | 11 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.86083 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.4005 | 31.1214 | 0 | 0 | 0
3 | 7 | 12 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.0053 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.256 | 27.9114 | 0 | 0 | 0
3 | 7 | 13 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.058 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.2033 | 26.7402 | 0 | 0 | 0
3 | 7 | 14 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.0248 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.2365 | 27.4776 | 0 | 0 | 0
3 | 7 | 15 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.90768 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.3536 | 30.0803 | 0 | 0 | 0
3 | 7 | 16 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.70662 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.5547 | 34.5482 | 0 | 0 | 0
3 | 7 | 17 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.47434 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.787 | 39.7102 | 0 | 0 | 0
3 | 7 | 18 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.24205 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.0192 | 44.8721 | 0 | 0 | 0
3 | 7 | 19 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.056608 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.2047 | 48.993 | 0 | 0 | 0
3 | 7 | 20 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 7 | 21 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 7 | 22 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 7 | 23 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 7 | 24 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 8 | 1 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 8 | 2 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 8 | 3 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 8 | 4 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 8 | 5 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 8 | 6 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 8 | 7 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.021472 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.2398 | 49.7738 | 0 | 0 | 0
3 | 8 | 8 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.19715 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.0641 | 45.8698 | 0 | 0 | 0
3 | 8 | 9 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.45286 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.8084 | 40.1873 | 0 | 0 | 0
3 | 8 | 10 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.71638 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.5449 | 34.3313 | 0 | 0 | 0
3 | 8 | 11 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.93696 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.3243 | 29.4296 | 0 | 0 | 0
3 | 8 | 12 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.0873 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.174 | 26.0895 | 0 | 0 | 0
3 | 8 | 13 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.1497 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.1116 | 24.7014 | 0 | 0 | 0
3 | 8 | 14 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.0951 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.1662 | 25.916 | 0 | 0 | 0
3 | 8 | 15 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.96624 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.2951 | 28.779 | 0 | 0 | 0
3 | 8 | 16 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.74762 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.5137 | 33.6373 | 0 | 0 | 0
3 | 8 | 17 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.488 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.7733 | 39.4065 | 0 | 0 | 0
3 | 8 | 18 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.22448 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.0368 | 45.2625 | 0 | 0 | 0
3 | 8 | 19 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.027328 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.234 | 49.6437 | 0 | 0 | 0
3 | 8 | 20 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 8 | 21 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 8 | 22 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 8 | 23 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 8 | 24 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 9 | 1 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 9 | 2 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 9 | 3 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 9 | 4 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 9 | 5 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 9 | 6 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 9 | 7 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.017568 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.2437 | 49.8606 | 0 | 0 | 0
3 | 9 | 8 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.25376 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.0075 | 44.6118 | 0 | 0 | 0
3 | 9 | 9 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.60512 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.6562 | 36.8038 | 0 | 0 | 0
3 | 9 | 10 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.9272 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.3341 | 29.6465 | 0 | 0 | 0
3 | 9 | 11 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.1712 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.0901 | 24.2243 | 0 | 0 | 0
3 | 9 | 12 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.3235 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.93784 | 20.8408 | 0 | 0 | 0
3 | 9 | 13 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.3684 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.89294 | 19.8431 | 0 | 0 | 0
3 | 9 | 14 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.2903 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.97102 | 21.5782 | 0 | 0 | 0
3 | 9 | 15 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.099 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.1623 | 25.8293 | 0 | 0 | 0
3 | 9 | 16 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.84326 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.418 | 31.5118 | 0 | 0 | 0
3 | 9 | 17 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.51533 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.746 | 38.7992 | 0 | 0 | 0
3 | 9 | 18 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.16787 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.0934 | 46.5205 | 0 | 0 | 0
3 | 9 | 19 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.001952 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.2593 | 50.2076 | 0 | 0 | 0
3 | 9 | 20 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 9 | 21 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 9 | 22 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 9 | 23 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 9 | 24 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 10 | 1 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 10 | 2 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 10 | 3 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 10 | 4 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 10 | 5 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 10 | 6 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 10 | 7 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 10 | 8 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.26742 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.9939 | 44.3082 | 0 | 0 | 0
3 | 10 | 9 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.71443 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.5469 | 34.3747 | 0 | 0 | 0
3 | 10 | 10 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.058 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.2033 | 26.7402 | 0 | 0 | 0
3 | 10 | 11 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.3059 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.95541 | 21.2312 | 0 | 0 | 0
3 | 10 | 12 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.4484 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.81291 | 18.0646 | 0 | 0 | 0
3 | 10 | 13 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.4718 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.78949 | 17.5441 | 0 | 0 | 0
3 | 10 | 14 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.3566 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.90465 | 20.1034 | 0 | 0 | 0
3 | 10 | 15 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.138 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.1233 | 24.9617 | 0 | 0 | 0
3 | 10 | 16 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.8335 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.4278 | 31.7286 | 0 | 0 | 0
3 | 10 | 17 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.46653 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.7948 | 39.8837 | 0 | 0 | 0
3 | 10 | 18 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.060512 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.2008 | 48.9062 | 0 | 0 | 0
3 | 10 | 19 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 10 | 20 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 10 | 21 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 10 | 22 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 10 | 23 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 10 | 24 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 11 | 1 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 11 | 2 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 11 | 3 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 11 | 4 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 11 | 5 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 11 | 6 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 11 | 7 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 11 | 8 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.15811 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.1032 | 46.7374 | 0 | 0 | 0
3 | 11 | 9 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.64221 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.6191 | 35.9797 | 0 | 0 | 0
3 | 11 | 10 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.0053 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.256 | 27.9114 | 0 | 0 | 0
3 | 11 | 11 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.2571 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.0042 | 22.3157 | 0 | 0 | 0
3 | 11 | 12 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.3957 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.86561 | 19.2358 | 0 | 0 | 0
3 | 11 | 13 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.4093 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.85195 | 18.9322 | 0 | 0 | 0
3 | 11 | 14 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.3117 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.94955 | 21.1011 | 0 | 0 | 0
3 | 11 | 15 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.0931 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.1682 | 25.9594 | 0 | 0 | 0
3 | 11 | 16 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.7847 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.4766 | 32.8131 | 0 | 0 | 0
3 | 11 | 17 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.3416 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.9197 | 42.6598 | 0 | 0 | 0
3 | 11 | 18 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 11 | 19 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 11 | 20 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 11 | 21 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 11 | 22 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 11 | 23 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 11 | 24 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 12 | 1 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 12 | 2 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 12 | 3 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 12 | 4 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 12 | 5 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 12 | 6 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 12 | 7 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 12 | 8 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.064416 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.1969 | 48.8195 | 0 | 0 | 0
3 | 12 | 9 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.5329 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.7284 | 38.4088 | 0 | 0 | 0
3 | 12 | 10 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.91158 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.3497 | 29.9935 | 0 | 0 | 0
3 | 12 | 11 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.1829 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.0784 | 23.964 | 0 | 0 | 0
3 | 12 | 12 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.3488 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.91246 | 20.2769 | 0 | 0 | 0
3 | 12 | 13 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.3937 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.86757 | 19.2792 | 0 | 0 | 0
3 | 12 | 14 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.3098 | 100 | 1.4325 | 100 | 1.773 | 100 | 0.9515 | 21.1445 | 0 | 0 | 0
3 | 12 | 15 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 1.1087 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.1526 | 25.6124 | 0 | 0 | 0
3 | 12 | 16 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.81789 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.4434 | 32.0757 | 0 | 0 | 0
3 | 12 | 17 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.37674 | 100 | 1.4325 | 100 | 1.773 | 100 | 1.8846 | 41.879 | 0 | 0 | 0
3 | 12 | 18 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0.003904 | 100 | 1.4325 | 100 | 1.773 | 100 | 2.2574 | 50.1642 | 0 | 0 | 0
3 | 12 | 19 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 12 | 20 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 12 | 21 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 12 | 22 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 12 | 23 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
3 | 12 | 24 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
4 | 1 | 1 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 1 | 2 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 1 | 3 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 1 | 4 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 1 | 5 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 1 | 6 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 1 | 7 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 1 | 8 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.042592 | 100 | 1.41 | 100 | 1.746 | 100 | 2.2773 | 50.6071 | 0 | 0 | 0
4 | 1 | 9 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.46464 | 100 | 1.41 | 100 | 1.746 | 100 | 1.8553 | 41.2283 | 0 | 0 | 0
4 | 1 | 10 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.85765 | 100 | 1.41 | 100 | 1.746 | 100 | 1.4623 | 32.4948 | 0 | 0 | 0
4 | 1 | 11 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.1539 | 100 | 1.41 | 100 | 1.746 | 100 | 1.1661 | 25.9124 | 0 | 0 | 0
4 | 1 | 12 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.3455 | 100 | 1.41 | 100 | 1.746 | 100 | 0.97439 | 21.6532 | 0 | 0 | 0
4 | 1 | 13 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.4172 | 100 | 1.41 | 100 | 1.746 | 100 | 0.90276 | 20.0614 | 0 | 0 | 0
4 | 1 | 14 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.3629 | 100 | 1.41 | 100 | 1.746 | 100 | 0.95697 | 21.266 | 0 | 0 | 0
4 | 1 | 15 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.1945 | 100 | 1.41 | 100 | 1.746 | 100 | 1.1254 | 25.0089 | 0 | 0 | 0
4 | 1 | 16 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.91186 | 100 | 1.41 | 100 | 1.746 | 100 | 1.4081 | 31.2902 | 0 | 0 | 0
4 | 1 | 17 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.54982 | 100 | 1.41 | 100 | 1.746 | 100 | 1.7701 | 39.3353 | 0 | 0 | 0
4 | 1 | 18 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.07744 | 100 | 1.41 | 100 | 1.746 | 100 | 2.2425 | 49.8327 | 0 | 0 | 0
4 | 1 | 19 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 1 | 20 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 1 | 21 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 1 | 22 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 1 | 23 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 1 | 24 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 2 | 1 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 2 | 2 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 2 | 3 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 2 | 4 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 2 | 5 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 2 | 6 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 2 | 7 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 2 | 8 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.069696 | 100 | 1.41 | 100 | 1.746 | 100 | 2.2502 | 50.0048 | 0 | 0 | 0
4 | 2 | 9 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.50723 | 100 | 1.41 | 100 | 1.746 | 100 | 1.8127 | 40.2818 | 0 | 0 | 0
4 | 2 | 10 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.90024 | 100 | 1.41 | 100 | 1.746 | 100 | 1.4197 | 31.5483 | 0 | 0 | 0
4 | 2 | 11 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.2081 | 100 | 1.41 | 100 | 1.746 | 100 | 1.1118 | 24.7078 | 0 | 0 | 0
4 | 2 | 12 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.4152 | 100 | 1.41 | 100 | 1.746 | 100 | 0.9047 | 20.1044 | 0 | 0 | 0
4 | 2 | 13 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.4965 | 100 | 1.41 | 100 | 1.746 | 100 | 0.82339 | 18.2975 | 0 | 0 | 0
4 | 2 | 14 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.4578 | 100 | 1.41 | 100 | 1.746 | 100 | 0.86211 | 19.1579 | 0 | 0 | 0
4 | 2 | 15 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.2971 | 100 | 1.41 | 100 | 1.746 | 100 | 1.0228 | 22.7287 | 0 | 0 | 0
4 | 2 | 16 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.03 | 100 | 1.41 | 100 | 1.746 | 100 | 1.29 | 28.6658 | 0 | 0 | 0
4 | 2 | 17 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.67179 | 100 | 1.41 | 100 | 1.746 | 100 | 1.6481 | 36.6249 | 0 | 0 | 0
4 | 2 | 18 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.17618 | 100 | 1.41 | 100 | 1.746 | 100 | 2.1437 | 47.6386 | 0 | 0 | 0
4 | 2 | 19 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 2 | 20 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 2 | 21 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 2 | 22 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 2 | 23 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 2 | 24 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 3 | 1 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 3 | 2 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 3 | 3 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 3 | 4 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 3 | 5 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 3 | 6 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 3 | 7 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.001936 | 100 | 1.41 | 100 | 1.746 | 100 | 2.318 | 51.5106 | 0 | 0 | 0
4 | 3 | 8 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.16069 | 100 | 1.41 | 100 | 1.746 | 100 | 2.1592 | 47.9828 | 0 | 0 | 0
4 | 3 | 9 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.58274 | 100 | 1.41 | 100 | 1.746 | 100 | 1.7372 | 38.6039 | 0 | 0 | 0
4 | 3 | 10 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.96026 | 100 | 1.41 | 100 | 1.746 | 100 | 1.3597 | 30.2146 | 0 | 0 | 0
4 | 3 | 11 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.2429 | 100 | 1.41 | 100 | 1.746 | 100 | 1.077 | 23.9334 | 0 | 0 | 0
4 | 3 | 12 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.4384 | 100 | 1.41 | 100 | 1.746 | 100 | 0.88147 | 19.5881 | 0 | 0 | 0
4 | 3 | 13 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.512 | 100 | 1.41 | 100 | 1.746 | 100 | 0.8079 | 17.9533 | 0 | 0 | 0
4 | 3 | 14 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.4772 | 100 | 1.41 | 100 | 1.746 | 100 | 0.84275 | 18.7277 | 0 | 0 | 0
4 | 3 | 15 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.2797 | 100 | 1.41 | 100 | 1.746 | 100 | 1.0402 | 23.1159 | 0 | 0 | 0
4 | 3 | 16 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.0145 | 100 | 1.41 | 100 | 1.746 | 100 | 1.3054 | 29.01 | 0 | 0 | 0
4 | 3 | 17 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.66405 | 100 | 1.41 | 100 | 1.746 | 100 | 1.6559 | 36.797 | 0 | 0 | 0
4 | 3 | 18 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.24974 | 100 | 1.41 | 100 | 1.746 | 100 | 2.0702 | 46.0038 | 0 | 0 | 0
4 | 3 | 19 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.001936 | 100 | 1.41 | 100 | 1.746 | 100 | 2.318 | 51.5106 | 0 | 0 | 0
4 | 3 | 20 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 3 | 21 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 3 | 22 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 3 | 23 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 3 | 24 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 4 | 1 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 4 | 2 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 4 | 3 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 4 | 4 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 4 | 5 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 4 | 6 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 4 | 7 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.02904 | 100 | 1.41 | 100 | 1.746 | 100 | 2.2909 | 50.9083 | 0 | 0 | 0
4 | 4 | 8 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.28072 | 100 | 1.41 | 100 | 1.746 | 100 | 2.0392 | 45.3154 | 0 | 0 | 0
4 | 4 | 9 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.64662 | 100 | 1.41 | 100 | 1.746 | 100 | 1.6733 | 37.1842 | 0 | 0 | 0
4 | 4 | 10 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.98349 | 100 | 1.41 | 100 | 1.746 | 100 | 1.3364 | 29.6983 | 0 | 0 | 0
4 | 4 | 11 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.2371 | 100 | 1.41 | 100 | 1.746 | 100 | 1.0828 | 24.0624 | 0 | 0 | 0
4 | 4 | 12 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.392 | 100 | 1.41 | 100 | 1.746 | 100 | 0.92793 | 20.6207 | 0 | 0 | 0
4 | 4 | 13 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.4404 | 100 | 1.41 | 100 | 1.746 | 100 | 0.87953 | 19.5451 | 0 | 0 | 0
4 | 4 | 14 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.3688 | 100 | 1.41 | 100 | 1.746 | 100 | 0.95116 | 21.1369 | 0 | 0 | 0
4 | 4 | 15 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.1964 | 100 | 1.41 | 100 | 1.746 | 100 | 1.1235 | 24.9659 | 0 | 0 | 0
4 | 4 | 16 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.92928 | 100 | 1.41 | 100 | 1.746 | 100 | 1.3906 | 30.903 | 0 | 0 | 0
4 | 4 | 17 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.6079 | 100 | 1.41 | 100 | 1.746 | 100 | 1.712 | 38.0447 | 0 | 0 | 0
4 | 4 | 18 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.25555 | 100 | 1.41 | 100 | 1.746 | 100 | 2.0644 | 45.8747 | 0 | 0 | 0
4 | 4 | 19 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.01936 | 100 | 1.41 | 100 | 1.746 | 100 | 2.3006 | 51.1234 | 0 | 0 | 0
4 | 4 | 20 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 4 | 21 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 4 | 22 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 4 | 23 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 4 | 24 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 5 | 1 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 5 | 2 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 5 | 3 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 5 | 4 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 5 | 5 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 5 | 6 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 5 | 7 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.069696 | 100 | 1.41 | 100 | 1.746 | 100 | 2.2502 | 50.0048 | 0 | 0 | 0
4 | 5 | 8 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.30976 | 100 | 1.41 | 100 | 1.746 | 100 | 2.0102 | 44.6701 | 0 | 0 | 0
4 | 5 | 9 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.63114 | 100 | 1.41 | 100 | 1.746 | 100 | 1.6888 | 37.5284 | 0 | 0 | 0
4 | 5 | 10 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.93315 | 100 | 1.41 | 100 | 1.746 | 100 | 1.3868 | 30.8169 | 0 | 0 | 0
4 | 5 | 11 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.1616 | 100 | 1.41 | 100 | 1.746 | 100 | 1.1583 | 25.7403 | 0 | 0 | 0
4 | 5 | 12 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.3029 | 100 | 1.41 | 100 | 1.746 | 100 | 1.017 | 22.5997 | 0 | 0 | 0
4 | 5 | 13 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.3416 | 100 | 1.41 | 100 | 1.746 | 100 | 0.97827 | 21.7392 | 0 | 0 | 0
4 | 5 | 14 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.2739 | 100 | 1.41 | 100 | 1.746 | 100 | 1.046 | 23.245 | 0 | 0 | 0
4 | 5 | 15 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.1113 | 100 | 1.41 | 100 | 1.746 | 100 | 1.2086 | 26.8589 | 0 | 0 | 0
4 | 5 | 16 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.86539 | 100 | 1.41 | 100 | 1.746 | 100 | 1.4545 | 32.3227 | 0 | 0 | 0
4 | 5 | 17 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.56144 | 100 | 1.41 | 100 | 1.746 | 100 | 1.7585 | 39.0772 | 0 | 0 | 0
4 | 5 | 18 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.25942 | 100 | 1.41 | 100 | 1.746 | 100 | 2.0605 | 45.7887 | 0 | 0 | 0
4 | 5 | 19 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.036784 | 100 | 1.41 | 100 | 1.746 | 100 | 2.2831 | 50.7362 | 0 | 0 | 0
4 | 5 | 20 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 5 | 21 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 5 | 22 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 5 | 23 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 5 | 24 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 6 | 1 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 6 | 2 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 6 | 3 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 6 | 4 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 6 | 5 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 6 | 6 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 6 | 7 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.06776 | 100 | 1.41 | 100 | 1.746 | 100 | 2.2522 | 50.0479 | 0 | 0 | 0
4 | 6 | 8 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.25555 | 100 | 1.41 | 100 | 1.746 | 100 | 2.0644 | 45.8747 | 0 | 0 | 0
4 | 6 | 9 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.52466 | 100 | 1.41 | 100 | 1.746 | 100 | 1.7953 | 39.8946 | 0 | 0 | 0
4 | 6 | 10 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.8015 | 100 | 1.41 | 100 | 1.746 | 100 | 1.5184 | 33.7424 | 0 | 0 | 0
4 | 6 | 11 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.0203 | 100 | 1.41 | 100 | 1.746 | 100 | 1.2996 | 28.8809 | 0 | 0 | 0
4 | 6 | 12 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.1519 | 100 | 1.41 | 100 | 1.746 | 100 | 1.168 | 25.9554 | 0 | 0 | 0
4 | 6 | 13 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.2061 | 100 | 1.41 | 100 | 1.746 | 100 | 1.1138 | 24.7508 | 0 | 0 | 0
4 | 6 | 14 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.15 | 100 | 1.41 | 100 | 1.746 | 100 | 1.1699 | 25.9984 | 0 | 0 | 0
4 | 6 | 15 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.0028 | 100 | 1.41 | 100 | 1.746 | 100 | 1.3171 | 29.2681 | 0 | 0 | 0
4 | 6 | 16 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.79376 | 100 | 1.41 | 100 | 1.746 | 100 | 1.5262 | 33.9145 | 0 | 0 | 0
4 | 6 | 17 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.53046 | 100 | 1.41 | 100 | 1.746 | 100 | 1.7894 | 39.7655 | 0 | 0 | 0
4 | 6 | 18 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.26136 | 100 | 1.41 | 100 | 1.746 | 100 | 2.0586 | 45.7456 | 0 | 0 | 0
4 | 6 | 19 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.054208 | 100 | 1.41 | 100 | 1.746 | 100 | 2.2657 | 50.349 | 0 | 0 | 0
4 | 6 | 20 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 6 | 21 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 6 | 22 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 6 | 23 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 6 | 24 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 7 | 1 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 7 | 2 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 7 | 3 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 7 | 4 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 7 | 5 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 7 | 6 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 7 | 7 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.036784 | 100 | 1.41 | 100 | 1.746 | 100 | 2.2831 | 50.7362 | 0 | 0 | 0
4 | 7 | 8 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.18973 | 100 | 1.41 | 100 | 1.746 | 100 | 2.1302 | 47.3375 | 0 | 0 | 0
4 | 7 | 9 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.41237 | 100 | 1.41 | 100 | 1.746 | 100 | 1.9075 | 42.3899 | 0 | 0 | 0
4 | 7 | 10 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.65243 | 100 | 1.41 | 100 | 1.746 | 100 | 1.6675 | 37.0551 | 0 | 0 | 0
4 | 7 | 11 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.85378 | 100 | 1.41 | 100 | 1.746 | 100 | 1.4661 | 32.5808 | 0 | 0 | 0
4 | 7 | 12 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.99704 | 100 | 1.41 | 100 | 1.746 | 100 | 1.3229 | 29.3972 | 0 | 0 | 0
4 | 7 | 13 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.0493 | 100 | 1.41 | 100 | 1.746 | 100 | 1.2706 | 28.2356 | 0 | 0 | 0
4 | 7 | 14 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.0164 | 100 | 1.41 | 100 | 1.746 | 100 | 1.3035 | 28.967 | 0 | 0 | 0
4 | 7 | 15 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.90024 | 100 | 1.41 | 100 | 1.746 | 100 | 1.4197 | 31.5483 | 0 | 0 | 0
4 | 7 | 16 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.70083 | 100 | 1.41 | 100 | 1.746 | 100 | 1.6191 | 35.9796 | 0 | 0 | 0
4 | 7 | 17 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.47045 | 100 | 1.41 | 100 | 1.746 | 100 | 1.8495 | 41.0992 | 0 | 0 | 0
4 | 7 | 18 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.24006 | 100 | 1.41 | 100 | 1.746 | 100 | 2.0798 | 46.2189 | 0 | 0 | 0
4 | 7 | 19 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.056144 | 100 | 1.41 | 100 | 1.746 | 100 | 2.2638 | 50.306 | 0 | 0 | 0
4 | 7 | 20 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 7 | 21 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 7 | 22 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 7 | 23 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 7 | 24 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 8 | 1 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 8 | 2 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 8 | 3 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 8 | 4 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 8 | 5 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 8 | 6 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 8 | 7 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.021296 | 100 | 1.41 | 100 | 1.746 | 100 | 2.2986 | 51.0804 | 0 | 0 | 0
4 | 8 | 8 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.19554 | 100 | 1.41 | 100 | 1.746 | 100 | 2.1244 | 47.2084 | 0 | 0 | 0
4 | 8 | 9 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.44915 | 100 | 1.41 | 100 | 1.746 | 100 | 1.8708 | 41.5725 | 0 | 0 | 0
4 | 8 | 10 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.71051 | 100 | 1.41 | 100 | 1.746 | 100 | 1.6094 | 35.7645 | 0 | 0 | 0
4 | 8 | 11 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.92928 | 100 | 1.41 | 100 | 1.746 | 100 | 1.3906 | 30.903 | 0 | 0 | 0
4 | 8 | 12 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.0784 | 100 | 1.41 | 100 | 1.746 | 100 | 1.2416 | 27.5903 | 0 | 0 | 0
4 | 8 | 13 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.1403 | 100 | 1.41 | 100 | 1.746 | 100 | 1.1796 | 26.2135 | 0 | 0 | 0
4 | 8 | 14 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.0861 | 100 | 1.41 | 100 | 1.746 | 100 | 1.2338 | 27.4182 | 0 | 0 | 0
4 | 8 | 15 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.95832 | 100 | 1.41 | 100 | 1.746 | 100 | 1.3616 | 30.2576 | 0 | 0 | 0
4 | 8 | 16 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.74149 | 100 | 1.41 | 100 | 1.746 | 100 | 1.5784 | 35.0761 | 0 | 0 | 0
4 | 8 | 17 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.484 | 100 | 1.41 | 100 | 1.746 | 100 | 1.8359 | 40.7981 | 0 | 0 | 0
4 | 8 | 18 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.22264 | 100 | 1.41 | 100 | 1.746 | 100 | 2.0973 | 46.6061 | 0 | 0 | 0
4 | 8 | 19 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.027104 | 100 | 1.41 | 100 | 1.746 | 100 | 2.2928 | 50.9513 | 0 | 0 | 0
4 | 8 | 20 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 8 | 21 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 8 | 22 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 8 | 23 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 8 | 24 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 9 | 1 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 9 | 2 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 9 | 3 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 9 | 4 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 9 | 5 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 9 | 6 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 9 | 7 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.017424 | 100 | 1.41 | 100 | 1.746 | 100 | 2.3025 | 51.1664 | 0 | 0 | 0
4 | 9 | 8 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.25168 | 100 | 1.41 | 100 | 1.746 | 100 | 2.0682 | 45.9607 | 0 | 0 | 0
4 | 9 | 9 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.60016 | 100 | 1.41 | 100 | 1.746 | 100 | 1.7198 | 38.2167 | 0 | 0 | 0
4 | 9 | 10 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.9196 | 100 | 1.41 | 100 | 1.746 | 100 | 1.4003 | 31.1181 | 0 | 0 | 0
4 | 9 | 11 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.1616 | 100 | 1.41 | 100 | 1.746 | 100 | 1.1583 | 25.7403 | 0 | 0 | 0
4 | 9 | 12 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.3126 | 100 | 1.41 | 100 | 1.746 | 100 | 1.0073 | 22.3846 | 0 | 0 | 0
4 | 9 | 13 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.3571 | 100 | 1.41 | 100 | 1.746 | 100 | 0.96278 | 21.3951 | 0 | 0 | 0
4 | 9 | 14 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.2797 | 100 | 1.41 | 100 | 1.746 | 100 | 1.0402 | 23.1159 | 0 | 0 | 0
4 | 9 | 15 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.09 | 100 | 1.41 | 100 | 1.746 | 100 | 1.2299 | 27.3321 | 0 | 0 | 0
4 | 9 | 16 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.83635 | 100 | 1.41 | 100 | 1.746 | 100 | 1.4836 | 32.968 | 0 | 0 | 0
4 | 9 | 17 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.5111 | 100 | 1.41 | 100 | 1.746 | 100 | 1.8088 | 40.1958 | 0 | 0 | 0
4 | 9 | 18 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.1665 | 100 | 1.41 | 100 | 1.746 | 100 | 2.1534 | 47.8537 | 0 | 0 | 0
4 | 9 | 19 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.001936 | 100 | 1.41 | 100 | 1.746 | 100 | 2.318 | 51.5106 | 0 | 0 | 0
4 | 9 | 20 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 9 | 21 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 9 | 22 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 9 | 23 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 9 | 24 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 10 | 1 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 10 | 2 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 10 | 3 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 10 | 4 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 10 | 5 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 10 | 6 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 10 | 7 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 10 | 8 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.26523 | 100 | 1.41 | 100 | 1.746 | 100 | 2.0547 | 45.6596 | 0 | 0 | 0
4 | 10 | 9 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.70858 | 100 | 1.41 | 100 | 1.746 | 100 | 1.6113 | 35.8075 | 0 | 0 | 0
4 | 10 | 10 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.0493 | 100 | 1.41 | 100 | 1.746 | 100 | 1.2706 | 28.2356 | 0 | 0 | 0
4 | 10 | 11 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.2952 | 100 | 1.41 | 100 | 1.746 | 100 | 1.0247 | 22.7718 | 0 | 0 | 0
4 | 10 | 12 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.4365 | 100 | 1.41 | 100 | 1.746 | 100 | 0.8834 | 19.6311 | 0 | 0 | 0
4 | 10 | 13 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.4597 | 100 | 1.41 | 100 | 1.746 | 100 | 0.86017 | 19.1149 | 0 | 0 | 0
4 | 10 | 14 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.3455 | 100 | 1.41 | 100 | 1.746 | 100 | 0.97439 | 21.6532 | 0 | 0 | 0
4 | 10 | 15 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.1287 | 100 | 1.41 | 100 | 1.746 | 100 | 1.1912 | 26.4717 | 0 | 0 | 0
4 | 10 | 16 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.82667 | 100 | 1.41 | 100 | 1.746 | 100 | 1.4932 | 33.1831 | 0 | 0 | 0
4 | 10 | 17 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.4627 | 100 | 1.41 | 100 | 1.746 | 100 | 1.8572 | 41.2713 | 0 | 0 | 0
4 | 10 | 18 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.060016 | 100 | 1.41 | 100 | 1.746 | 100 | 2.2599 | 50.2199 | 0 | 0 | 0
4 | 10 | 19 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 10 | 20 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 10 | 21 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 10 | 22 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 10 | 23 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 10 | 24 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 11 | 1 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 11 | 2 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 11 | 3 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 11 | 4 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 11 | 5 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 11 | 6 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 11 | 7 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 11 | 8 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.15682 | 100 | 1.41 | 100 | 1.746 | 100 | 2.1631 | 48.0688 | 0 | 0 | 0
4 | 11 | 9 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.63694 | 100 | 1.41 | 100 | 1.746 | 100 | 1.683 | 37.3993 | 0 | 0 | 0
4 | 11 | 10 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.99704 | 100 | 1.41 | 100 | 1.746 | 100 | 1.3229 | 29.3972 | 0 | 0 | 0
4 | 11 | 11 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.2468 | 100 | 1.41 | 100 | 1.746 | 100 | 1.0731 | 23.8473 | 0 | 0 | 0
4 | 11 | 12 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.3842 | 100 | 1.41 | 100 | 1.746 | 100 | 0.93567 | 20.7927 | 0 | 0 | 0
4 | 11 | 13 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.3978 | 100 | 1.41 | 100 | 1.746 | 100 | 0.92212 | 20.4916 | 0 | 0 | 0
4 | 11 | 14 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.301 | 100 | 1.41 | 100 | 1.746 | 100 | 1.0189 | 22.6427 | 0 | 0 | 0
4 | 11 | 15 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.0842 | 100 | 1.41 | 100 | 1.746 | 100 | 1.2358 | 27.4612 | 0 | 0 | 0
4 | 11 | 16 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.77827 | 100 | 1.41 | 100 | 1.746 | 100 | 1.5416 | 34.2587 | 0 | 0 | 0
4 | 11 | 17 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.3388 | 100 | 1.41 | 100 | 1.746 | 100 | 1.9811 | 44.0247 | 0 | 0 | 0
4 | 11 | 18 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 11 | 19 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 11 | 20 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 11 | 21 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 11 | 22 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 11 | 23 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 11 | 24 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 12 | 1 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 12 | 2 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 12 | 3 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 12 | 4 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 12 | 5 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 12 | 6 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 12 | 7 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 12 | 8 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.063888 | 100 | 1.41 | 100 | 1.746 | 100 | 2.256 | 50.1339 | 0 | 0 | 0
4 | 12 | 9 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.52853 | 100 | 1.41 | 100 | 1.746 | 100 | 1.7914 | 39.8086 | 0 | 0 | 0
4 | 12 | 10 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.90411 | 100 | 1.41 | 100 | 1.746 | 100 | 1.4158 | 31.4623 | 0 | 0 | 0
4 | 12 | 11 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.1732 | 100 | 1.41 | 100 | 1.746 | 100 | 1.1467 | 25.4822 | 0 | 0 | 0
4 | 12 | 12 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.3378 | 100 | 1.41 | 100 | 1.746 | 100 | 0.98214 | 21.8253 | 0 | 0 | 0
4 | 12 | 13 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.3823 | 100 | 1.41 | 100 | 1.746 | 100 | 0.93761 | 20.8358 | 0 | 0 | 0
4 | 12 | 14 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.2991 | 100 | 1.41 | 100 | 1.746 | 100 | 1.0209 | 22.6857 | 0 | 0 | 0
4 | 12 | 15 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 1.0996 | 100 | 1.41 | 100 | 1.746 | 100 | 1.2203 | 27.117 | 0 | 0 | 0
4 | 12 | 16 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.81118 | 100 | 1.41 | 100 | 1.746 | 100 | 1.5087 | 33.5273 | 0 | 0 | 0
4 | 12 | 17 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.37365 | 100 | 1.41 | 100 | 1.746 | 100 | 1.9463 | 43.2503 | 0 | 0 | 0
4 | 12 | 18 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.003872 | 100 | 1.41 | 100 | 1.746 | 100 | 2.316 | 51.4676 | 0 | 0 | 0
4 | 12 | 19 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 12 | 20 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 12 | 21 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 12 | 22 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 12 | 23 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
4 | 12 | 24 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0 | 0 | 1.41 | 100 | 1.746 | 100 | 2.3199 | 51.5536 | 0 | 0 | 0
5 | 1 | 1 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 1 | 2 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 1 | 3 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 1 | 4 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 1 | 5 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 1 | 6 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 1 | 7 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 1 | 8 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.04224 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3363 | 96.3621 | 0 | 0 | 0
5 | 1 | 9 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.4608 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.9177 | 87.0607 | 0 | 0 | 0
5 | 1 | 10 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.85056 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.528 | 78.3994 | 0 | 0 | 0
5 | 1 | 11 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.1443 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.2342 | 71.8714 | 0 | 0 | 0
5 | 1 | 12 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.3344 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.0441 | 67.6474 | 0 | 0 | 0
5 | 1 | 13 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.4054 | 100 | 1.3875 | 100 | 1.719 | 100 | 2.9731 | 66.0687 | 0 | 0 | 0
5 | 1 | 14 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.3517 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.0269 | 67.2634 | 0 | 0 | 0
5 | 1 | 15 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.1846 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.1939 | 70.9754 | 0 | 0 | 0
5 | 1 | 16 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.90432 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.4742 | 77.2047 | 0 | 0 | 0
5 | 1 | 17 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.54528 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.8333 | 85.1834 | 0 | 0 | 0
5 | 1 | 18 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.0768 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3017 | 95.5941 | 0 | 0 | 0
5 | 1 | 19 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 1 | 20 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 1 | 21 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 1 | 22 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 1 | 23 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 1 | 24 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 2 | 1 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 2 | 2 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 2 | 3 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 2 | 4 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 2 | 5 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 2 | 6 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 2 | 7 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 2 | 8 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.06912 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3094 | 95.7647 | 0 | 0 | 0
5 | 2 | 9 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.50304 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.8755 | 86.1221 | 0 | 0 | 0
5 | 2 | 10 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.8928 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.4857 | 77.4607 | 0 | 0 | 0
5 | 2 | 11 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.1981 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.1805 | 70.6767 | 0 | 0 | 0
5 | 2 | 12 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.4035 | 100 | 1.3875 | 100 | 1.719 | 100 | 2.975 | 66.1114 | 0 | 0 | 0
5 | 2 | 13 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.4842 | 100 | 1.3875 | 100 | 1.719 | 100 | 2.8944 | 64.3194 | 0 | 0 | 0
5 | 2 | 14 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.4458 | 100 | 1.3875 | 100 | 1.719 | 100 | 2.9328 | 65.1727 | 0 | 0 | 0
5 | 2 | 15 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.2864 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.0921 | 68.7141 | 0 | 0 | 0
5 | 2 | 16 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.0214 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.3571 | 74.6021 | 0 | 0 | 0
5 | 2 | 17 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.66624 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.7123 | 82.4954 | 0 | 0 | 0
5 | 2 | 18 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.17472 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.2038 | 93.4181 | 0 | 0 | 0
5 | 2 | 19 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 2 | 20 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 2 | 21 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 2 | 22 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 2 | 23 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 2 | 24 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 3 | 1 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 3 | 2 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 3 | 3 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 3 | 4 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 3 | 5 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 3 | 6 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 3 | 7 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.00192 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3766 | 97.2581 | 0 | 0 | 0
5 | 3 | 8 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.15936 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.2192 | 93.7594 | 0 | 0 | 0
5 | 3 | 9 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.57792 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.8006 | 84.4581 | 0 | 0 | 0
5 | 3 | 10 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.95232 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.4262 | 76.1381 | 0 | 0 | 0
5 | 3 | 11 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.2326 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.1459 | 69.9087 | 0 | 0 | 0
5 | 3 | 12 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.4266 | 100 | 1.3875 | 100 | 1.719 | 100 | 2.952 | 65.5994 | 0 | 0 | 0
5 | 3 | 13 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.4995 | 100 | 1.3875 | 100 | 1.719 | 100 | 2.879 | 63.9781 | 0 | 0 | 0
5 | 3 | 14 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.465 | 100 | 1.3875 | 100 | 1.719 | 100 | 2.9136 | 64.7461 | 0 | 0 | 0
5 | 3 | 15 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.2691 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.1094 | 69.0981 | 0 | 0 | 0
5 | 3 | 16 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.0061 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.3725 | 74.9434 | 0 | 0 | 0
5 | 3 | 17 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.65856 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.72 | 82.6661 | 0 | 0 | 0
5 | 3 | 18 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.24768 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.1309 | 91.7967 | 0 | 0 | 0
5 | 3 | 19 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.00192 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3766 | 97.2581 | 0 | 0 | 0
5 | 3 | 20 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 3 | 21 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 3 | 22 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 3 | 23 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 3 | 24 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 4 | 1 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 4 | 2 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 4 | 3 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 4 | 4 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 4 | 5 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 4 | 6 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 4 | 7 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.0288 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3497 | 96.6607 | 0 | 0 | 0
5 | 4 | 8 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.2784 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.1001 | 91.1141 | 0 | 0 | 0
5 | 4 | 9 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.64128 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.7373 | 83.0501 | 0 | 0 | 0
5 | 4 | 10 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.97536 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.4032 | 75.6261 | 0 | 0 | 0
5 | 4 | 11 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.2269 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.1517 | 70.0367 | 0 | 0 | 0
5 | 4 | 12 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.3805 | 100 | 1.3875 | 100 | 1.719 | 100 | 2.9981 | 66.6234 | 0 | 0 | 0
5 | 4 | 13 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.4285 | 100 | 1.3875 | 100 | 1.719 | 100 | 2.9501 | 65.5567 | 0 | 0 | 0
5 | 4 | 14 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.3574 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.0211 | 67.1354 | 0 | 0 | 0
5 | 4 | 15 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.1866 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.192 | 70.9327 | 0 | 0 | 0
5 | 4 | 16 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.9216 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.4569 | 76.8207 | 0 | 0 | 0
5 | 4 | 17 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.60288 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.7757 | 83.9034 | 0 | 0 | 0
5 | 4 | 18 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.25344 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.1251 | 91.6687 | 0 | 0 | 0
5 | 4 | 19 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.0192 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3593 | 96.8741 | 0 | 0 | 0
5 | 4 | 20 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 4 | 21 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 4 | 22 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 4 | 23 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 4 | 24 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 5 | 1 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 5 | 2 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 5 | 3 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 5 | 4 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 5 | 5 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 5 | 6 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 5 | 7 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.06912 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3094 | 95.7647 | 0 | 0 | 0
5 | 5 | 8 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.3072 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.0713 | 90.4741 | 0 | 0 | 0
5 | 5 | 9 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.62592 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.7526 | 83.3914 | 0 | 0 | 0
5 | 5 | 10 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.92544 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.4531 | 76.7354 | 0 | 0 | 0
5 | 5 | 11 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.152 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.2265 | 71.7007 | 0 | 0 | 0
5 | 5 | 12 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.2922 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.0864 | 68.5861 | 0 | 0 | 0
5 | 5 | 13 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.3306 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.048 | 67.7327 | 0 | 0 | 0
5 | 5 | 14 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.2634 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.1152 | 69.2261 | 0 | 0 | 0
5 | 5 | 15 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.1021 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.2765 | 72.8101 | 0 | 0 | 0
5 | 5 | 16 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.85824 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.5203 | 78.2287 | 0 | 0 | 0
5 | 5 | 17 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.5568 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.8217 | 84.9274 | 0 | 0 | 0
5 | 5 | 18 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.25728 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.1213 | 91.5834 | 0 | 0 | 0
5 | 5 | 19 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.03648 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3421 | 96.4901 | 0 | 0 | 0
5 | 5 | 20 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 5 | 21 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 5 | 22 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 5 | 23 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 5 | 24 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 6 | 1 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 6 | 2 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 6 | 3 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 6 | 4 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 6 | 5 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 6 | 6 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 6 | 7 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.0672 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3113 | 95.8074 | 0 | 0 | 0
5 | 6 | 8 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.25344 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.1251 | 91.6687 | 0 | 0 | 0
5 | 6 | 9 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.52032 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.8582 | 85.7381 | 0 | 0 | 0
5 | 6 | 10 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.79488 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.5837 | 79.6367 | 0 | 0 | 0
5 | 6 | 11 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.0118 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.3667 | 74.8154 | 0 | 0 | 0
5 | 6 | 12 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.1424 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.2361 | 71.9141 | 0 | 0 | 0
5 | 6 | 13 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.1962 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.1824 | 70.7194 | 0 | 0 | 0
5 | 6 | 14 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.1405 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.2381 | 71.9567 | 0 | 0 | 0
5 | 6 | 15 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.99456 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.384 | 75.1994 | 0 | 0 | 0
5 | 6 | 16 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.7872 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.5913 | 79.8074 | 0 | 0 | 0
5 | 6 | 17 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.52608 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.8525 | 85.6101 | 0 | 0 | 0
5 | 6 | 18 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.2592 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.1193 | 91.5407 | 0 | 0 | 0
5 | 6 | 19 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.05376 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3248 | 96.1061 | 0 | 0 | 0
5 | 6 | 20 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 6 | 21 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 6 | 22 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 6 | 23 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 6 | 24 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 7 | 1 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 7 | 2 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 7 | 3 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 7 | 4 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 7 | 5 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 7 | 6 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 7 | 7 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.03648 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3421 | 96.4901 | 0 | 0 | 0
5 | 7 | 8 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.18816 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.1904 | 93.1194 | 0 | 0 | 0
5 | 7 | 9 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.40896 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.9696 | 88.2127 | 0 | 0 | 0
5 | 7 | 10 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.64704 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.7315 | 82.9221 | 0 | 0 | 0
5 | 7 | 11 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.84672 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.5318 | 78.4847 | 0 | 0 | 0
5 | 7 | 12 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.9888 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.3897 | 75.3274 | 0 | 0 | 0
5 | 7 | 13 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.0406 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.3379 | 74.1754 | 0 | 0 | 0
5 | 7 | 14 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.008 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.3705 | 74.9007 | 0 | 0 | 0
5 | 7 | 15 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.8928 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.4857 | 77.4607 | 0 | 0 | 0
5 | 7 | 16 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.69504 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.6835 | 81.8554 | 0 | 0 | 0
5 | 7 | 17 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.46656 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.912 | 86.9327 | 0 | 0 | 0
5 | 7 | 18 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.23808 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.1405 | 92.0101 | 0 | 0 | 0
5 | 7 | 19 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.05568 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3229 | 96.0634 | 0 | 0 | 0
5 | 7 | 20 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 7 | 21 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 7 | 22 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 7 | 23 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 7 | 24 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 8 | 1 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 8 | 2 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 8 | 3 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 8 | 4 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 8 | 5 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 8 | 6 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 8 | 7 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.02112 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3574 | 96.8314 | 0 | 0 | 0
5 | 8 | 8 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.19392 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.1846 | 92.9914 | 0 | 0 | 0
5 | 8 | 9 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.44544 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.9331 | 87.4021 | 0 | 0 | 0
5 | 8 | 10 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.70464 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.6739 | 81.6421 | 0 | 0 | 0
5 | 8 | 11 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.9216 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.4569 | 76.8207 | 0 | 0 | 0
5 | 8 | 12 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.0694 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.3091 | 73.5354 | 0 | 0 | 0
5 | 8 | 13 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.1309 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.2477 | 72.1701 | 0 | 0 | 0
5 | 8 | 14 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.0771 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.3014 | 73.3647 | 0 | 0 | 0
5 | 8 | 15 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.9504 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.4281 | 76.1807 | 0 | 0 | 0
5 | 8 | 16 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.73536 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.6432 | 80.9594 | 0 | 0 | 0
5 | 8 | 17 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.48 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.8985 | 86.6341 | 0 | 0 | 0
5 | 8 | 18 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.2208 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.1577 | 92.3941 | 0 | 0 | 0
5 | 8 | 19 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.02688 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3517 | 96.7034 | 0 | 0 | 0
5 | 8 | 20 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 8 | 21 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 8 | 22 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 8 | 23 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 8 | 24 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 9 | 1 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 9 | 2 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 9 | 3 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 9 | 4 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 9 | 5 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 9 | 6 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 9 | 7 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.01728 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3613 | 96.9167 | 0 | 0 | 0
5 | 9 | 8 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.2496 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.1289 | 91.7541 | 0 | 0 | 0
5 | 9 | 9 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.5952 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.7833 | 84.0741 | 0 | 0 | 0
5 | 9 | 10 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.912 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.4665 | 77.0341 | 0 | 0 | 0
5 | 9 | 11 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.152 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.2265 | 71.7007 | 0 | 0 | 0
5 | 9 | 12 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.3018 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.0768 | 68.3727 | 0 | 0 | 0
5 | 9 | 13 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.3459 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.0326 | 67.3914 | 0 | 0 | 0
5 | 9 | 14 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.2691 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.1094 | 69.0981 | 0 | 0 | 0
5 | 9 | 15 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.081 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.2976 | 73.2794 | 0 | 0 | 0
5 | 9 | 16 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.82944 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.5491 | 78.8687 | 0 | 0 | 0
5 | 9 | 17 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.50688 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.8717 | 86.0367 | 0 | 0 | 0
5 | 9 | 18 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.16512 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.2134 | 93.6314 | 0 | 0 | 0
5 | 9 | 19 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.00192 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3766 | 97.2581 | 0 | 0 | 0
5 | 9 | 20 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 9 | 21 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 9 | 22 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 9 | 23 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 9 | 24 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 10 | 1 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 10 | 2 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 10 | 3 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 10 | 4 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 10 | 5 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 10 | 6 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 10 | 7 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 10 | 8 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.26304 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.1155 | 91.4554 | 0 | 0 | 0
5 | 10 | 9 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.70272 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.6758 | 81.6847 | 0 | 0 | 0
5 | 10 | 10 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.0406 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.3379 | 74.1754 | 0 | 0 | 0
5 | 10 | 11 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.2845 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.0941 | 68.7567 | 0 | 0 | 0
5 | 10 | 12 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.4246 | 100 | 1.3875 | 100 | 1.719 | 100 | 2.9539 | 65.6421 | 0 | 0 | 0
5 | 10 | 13 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.4477 | 100 | 1.3875 | 100 | 1.719 | 100 | 2.9309 | 65.1301 | 0 | 0 | 0
5 | 10 | 14 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.3344 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.0441 | 67.6474 | 0 | 0 | 0
5 | 10 | 15 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.1194 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.2592 | 72.4261 | 0 | 0 | 0
5 | 10 | 16 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.81984 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.5587 | 79.0821 | 0 | 0 | 0
5 | 10 | 17 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.45888 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.9197 | 87.1034 | 0 | 0 | 0
5 | 10 | 18 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.05952 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.319 | 95.9781 | 0 | 0 | 0
5 | 10 | 19 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 10 | 20 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 10 | 21 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 10 | 22 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 10 | 23 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 10 | 24 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 11 | 1 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 11 | 2 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 11 | 3 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 11 | 4 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 11 | 5 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 11 | 6 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 11 | 7 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 11 | 8 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.15552 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.223 | 93.8447 | 0 | 0 | 0
5 | 11 | 9 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.63168 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.7469 | 83.2634 | 0 | 0 | 0
5 | 11 | 10 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.9888 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.3897 | 75.3274 | 0 | 0 | 0
5 | 11 | 11 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.2365 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.1421 | 69.8234 | 0 | 0 | 0
5 | 11 | 12 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.3728 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.0057 | 66.7941 | 0 | 0 | 0
5 | 11 | 13 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.3862 | 100 | 1.3875 | 100 | 1.719 | 100 | 2.9923 | 66.4954 | 0 | 0 | 0
5 | 11 | 14 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.2902 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.0883 | 68.6287 | 0 | 0 | 0
5 | 11 | 15 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.0752 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.3033 | 73.4074 | 0 | 0 | 0
5 | 11 | 16 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.77184 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.6067 | 80.1487 | 0 | 0 | 0
5 | 11 | 17 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.336 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.0425 | 89.8341 | 0 | 0 | 0
5 | 11 | 18 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 11 | 19 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 11 | 20 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 11 | 21 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 11 | 22 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 11 | 23 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 11 | 24 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 12 | 1 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 12 | 2 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 12 | 3 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 12 | 4 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 12 | 5 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 12 | 6 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 12 | 7 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 12 | 8 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.06336 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3152 | 95.8927 | 0 | 0 | 0
5 | 12 | 9 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.52416 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.8544 | 85.6527 | 0 | 0 | 0
5 | 12 | 10 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.89664 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.4819 | 77.3754 | 0 | 0 | 0
5 | 12 | 11 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.1635 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.215 | 71.4447 | 0 | 0 | 0
5 | 12 | 12 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.3267 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.0518 | 67.8181 | 0 | 0 | 0
5 | 12 | 13 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.3709 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.0077 | 66.8367 | 0 | 0 | 0
5 | 12 | 14 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.2883 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.0902 | 68.6714 | 0 | 0 | 0
5 | 12 | 15 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 1.0906 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.288 | 73.0661 | 0 | 0 | 0
5 | 12 | 16 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.80448 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.5741 | 79.4234 | 0 | 0 | 0
5 | 12 | 17 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.37056 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.008 | 89.0661 | 0 | 0 | 0
5 | 12 | 18 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.00384 | 100 | 1.3875 | 100 | 1.719 | 100 | 4.3747 | 97.2154 | 0 | 0 | 0
5 | 12 | 19 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 12 | 20 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 12 | 21 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 12 | 22 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 12 | 23 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
5 | 12 | 24 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0 | 0 | 1.3875 | 100 | 1.719 | 100 | 4.3785 | 97.3007 | 0 | 0 | 0
6 | 1 | 1 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 1 | 2 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 1 | 3 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 1 | 4 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 1 | 5 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 1 | 6 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 1 | 7 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 1 | 8 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.041888 | 100 | 1.365 | 100 | 1.692 | 100 | 4.3953 | 97.6726 | 0 | 0 | 0
6 | 1 | 9 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.45696 | 100 | 1.365 | 100 | 1.692 | 100 | 3.9802 | 88.4488 | 0 | 0 | 0
6 | 1 | 10 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.84347 | 100 | 1.365 | 100 | 1.692 | 100 | 3.5937 | 79.8596 | 0 | 0 | 0
6 | 1 | 11 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.1348 | 100 | 1.365 | 100 | 1.692 | 100 | 3.3024 | 73.386 | 0 | 0 | 0
6 | 1 | 12 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.3233 | 100 | 1.365 | 100 | 1.692 | 100 | 3.1139 | 69.1972 | 0 | 0 | 0
6 | 1 | 13 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.3937 | 100 | 1.365 | 100 | 1.692 | 100 | 3.0434 | 67.6317 | 0 | 0 | 0
6 | 1 | 14 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.3404 | 100 | 1.365 | 100 | 1.692 | 100 | 3.0967 | 68.8164 | 0 | 0 | 0
6 | 1 | 15 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.1748 | 100 | 1.365 | 100 | 1.692 | 100 | 3.2624 | 72.4975 | 0 | 0 | 0
6 | 1 | 16 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.89678 | 100 | 1.365 | 100 | 1.692 | 100 | 3.5404 | 78.6749 | 0 | 0 | 0
6 | 1 | 17 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.54074 | 100 | 1.365 | 100 | 1.692 | 100 | 3.8964 | 86.5871 | 0 | 0 | 0
6 | 1 | 18 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.07616 | 100 | 1.365 | 100 | 1.692 | 100 | 4.361 | 96.911 | 0 | 0 | 0
6 | 1 | 19 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 1 | 20 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 1 | 21 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 1 | 22 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 1 | 23 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 1 | 24 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 2 | 1 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 2 | 2 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 2 | 3 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 2 | 4 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 2 | 5 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 2 | 6 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 2 | 7 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 2 | 8 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.068544 | 100 | 1.365 | 100 | 1.692 | 100 | 4.3686 | 97.0802 | 0 | 0 | 0
6 | 2 | 9 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.49885 | 100 | 1.365 | 100 | 1.692 | 100 | 3.9383 | 87.5179 | 0 | 0 | 0
6 | 2 | 10 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.88536 | 100 | 1.365 | 100 | 1.692 | 100 | 3.5518 | 78.9288 | 0 | 0 | 0
6 | 2 | 11 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.1881 | 100 | 1.365 | 100 | 1.692 | 100 | 3.2491 | 72.2013 | 0 | 0 | 0
6 | 2 | 12 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.3918 | 100 | 1.365 | 100 | 1.692 | 100 | 3.0453 | 67.674 | 0 | 0 | 0
6 | 2 | 13 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.4718 | 100 | 1.365 | 100 | 1.692 | 100 | 2.9654 | 65.8969 | 0 | 0 | 0
6 | 2 | 14 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.4337 | 100 | 1.365 | 100 | 1.692 | 100 | 3.0034 | 66.7432 | 0 | 0 | 0
6 | 2 | 15 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.2757 | 100 | 1.365 | 100 | 1.692 | 100 | 3.1615 | 70.255 | 0 | 0 | 0
6 | 2 | 16 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.0129 | 100 | 1.365 | 100 | 1.692 | 100 | 3.4242 | 76.0939 | 0 | 0 | 0
6 | 2 | 17 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.66069 | 100 | 1.365 | 100 | 1.692 | 100 | 3.7765 | 83.9215 | 0 | 0 | 0
6 | 2 | 18 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.17326 | 100 | 1.365 | 100 | 1.692 | 100 | 4.2639 | 94.7531 | 0 | 0 | 0
6 | 2 | 19 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 2 | 20 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 2 | 21 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 2 | 22 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 2 | 23 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 2 | 24 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 3 | 1 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 3 | 2 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 3 | 3 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 3 | 4 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 3 | 5 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 3 | 6 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 3 | 7 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.001904 | 100 | 1.365 | 100 | 1.692 | 100 | 4.4352 | 98.5611 | 0 | 0 | 0
6 | 3 | 8 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.15803 | 100 | 1.365 | 100 | 1.692 | 100 | 4.2791 | 95.0916 | 0 | 0 | 0
6 | 3 | 9 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.5731 | 100 | 1.365 | 100 | 1.692 | 100 | 3.864 | 85.8678 | 0 | 0 | 0
6 | 3 | 10 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.94438 | 100 | 1.365 | 100 | 1.692 | 100 | 3.4928 | 77.6171 | 0 | 0 | 0
6 | 3 | 11 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.2224 | 100 | 1.365 | 100 | 1.692 | 100 | 3.2148 | 71.4397 | 0 | 0 | 0
6 | 3 | 12 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.4147 | 100 | 1.365 | 100 | 1.692 | 100 | 3.0225 | 67.1663 | 0 | 0 | 0
6 | 3 | 13 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.487 | 100 | 1.365 | 100 | 1.692 | 100 | 2.9501 | 65.5584 | 0 | 0 | 0
6 | 3 | 14 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.4528 | 100 | 1.365 | 100 | 1.692 | 100 | 2.9844 | 66.32 | 0 | 0 | 0
6 | 3 | 15 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.2585 | 100 | 1.365 | 100 | 1.692 | 100 | 3.1786 | 70.6358 | 0 | 0 | 0
6 | 3 | 16 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.9977 | 100 | 1.365 | 100 | 1.692 | 100 | 3.4395 | 76.4324 | 0 | 0 | 0
6 | 3 | 17 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.65307 | 100 | 1.365 | 100 | 1.692 | 100 | 3.7841 | 84.0907 | 0 | 0 | 0
6 | 3 | 18 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.24562 | 100 | 1.365 | 100 | 1.692 | 100 | 4.1915 | 93.1453 | 0 | 0 | 0
6 | 3 | 19 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.001904 | 100 | 1.365 | 100 | 1.692 | 100 | 4.4352 | 98.5611 | 0 | 0 | 0
6 | 3 | 20 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 3 | 21 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 3 | 22 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 3 | 23 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 3 | 24 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 4 | 1 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 4 | 2 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 4 | 3 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 4 | 4 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 4 | 5 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 4 | 6 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 4 | 7 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.02856 | 100 | 1.365 | 100 | 1.692 | 100 | 4.4086 | 97.9688 | 0 | 0 | 0
6 | 4 | 8 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.27608 | 100 | 1.365 | 100 | 1.692 | 100 | 4.1611 | 92.4683 | 0 | 0 | 0
6 | 4 | 9 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.63594 | 100 | 1.365 | 100 | 1.692 | 100 | 3.8012 | 84.4715 | 0 | 0 | 0
6 | 4 | 10 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.96723 | 100 | 1.365 | 100 | 1.692 | 100 | 3.4699 | 77.1094 | 0 | 0 | 0
6 | 4 | 11 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.2167 | 100 | 1.365 | 100 | 1.692 | 100 | 3.2205 | 71.5666 | 0 | 0 | 0
6 | 4 | 12 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.369 | 100 | 1.365 | 100 | 1.692 | 100 | 3.0682 | 68.1817 | 0 | 0 | 0
6 | 4 | 13 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.4166 | 100 | 1.365 | 100 | 1.692 | 100 | 3.0206 | 67.124 | 0 | 0 | 0
6 | 4 | 14 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.3461 | 100 | 1.365 | 100 | 1.692 | 100 | 3.091 | 68.6895 | 0 | 0 | 0
6 | 4 | 15 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.1767 | 100 | 1.365 | 100 | 1.692 | 100 | 3.2605 | 72.4552 | 0 | 0 | 0
6 | 4 | 16 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.91392 | 100 | 1.365 | 100 | 1.692 | 100 | 3.5232 | 78.2941 | 0 | 0 | 0
6 | 4 | 17 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.59786 | 100 | 1.365 | 100 | 1.692 | 100 | 3.8393 | 85.3177 | 0 | 0 | 0
6 | 4 | 18 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.25133 | 100 | 1.365 | 100 | 1.692 | 100 | 4.1858 | 93.0184 | 0 | 0 | 0
6 | 4 | 19 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.01904 | 100 | 1.365 | 100 | 1.692 | 100 | 4.4181 | 98.1803 | 0 | 0 | 0
6 | 4 | 20 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 4 | 21 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 4 | 22 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 4 | 23 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 4 | 24 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 5 | 1 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 5 | 2 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 5 | 3 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 5 | 4 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 5 | 5 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 5 | 6 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 5 | 7 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.068544 | 100 | 1.365 | 100 | 1.692 | 100 | 4.3686 | 97.0802 | 0 | 0 | 0
6 | 5 | 8 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.30464 | 100 | 1.365 | 100 | 1.692 | 100 | 4.1325 | 91.8336 | 0 | 0 | 0
6 | 5 | 9 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.6207 | 100 | 1.365 | 100 | 1.692 | 100 | 3.8164 | 84.81 | 0 | 0 | 0
6 | 5 | 10 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.91773 | 100 | 1.365 | 100 | 1.692 | 100 | 3.5194 | 78.2095 | 0 | 0 | 0
6 | 5 | 11 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.1424 | 100 | 1.365 | 100 | 1.692 | 100 | 3.2948 | 73.2168 | 0 | 0 | 0
6 | 5 | 12 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.2814 | 100 | 1.365 | 100 | 1.692 | 100 | 3.1558 | 70.128 | 0 | 0 | 0
6 | 5 | 13 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.3195 | 100 | 1.365 | 100 | 1.692 | 100 | 3.1177 | 69.2818 | 0 | 0 | 0
6 | 5 | 14 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.2528 | 100 | 1.365 | 100 | 1.692 | 100 | 3.1843 | 70.7627 | 0 | 0 | 0
6 | 5 | 15 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.0929 | 100 | 1.365 | 100 | 1.692 | 100 | 3.3443 | 74.3168 | 0 | 0 | 0
6 | 5 | 16 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.85109 | 100 | 1.365 | 100 | 1.692 | 100 | 3.5861 | 79.6904 | 0 | 0 | 0
6 | 5 | 17 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.55216 | 100 | 1.365 | 100 | 1.692 | 100 | 3.885 | 86.3332 | 0 | 0 | 0
6 | 5 | 18 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.25514 | 100 | 1.365 | 100 | 1.692 | 100 | 4.182 | 92.9337 | 0 | 0 | 0
6 | 5 | 19 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.036176 | 100 | 1.365 | 100 | 1.692 | 100 | 4.401 | 97.7995 | 0 | 0 | 0
6 | 5 | 20 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 5 | 21 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 5 | 22 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 5 | 23 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 5 | 24 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 6 | 1 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 6 | 2 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 6 | 3 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 6 | 4 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 6 | 5 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 6 | 6 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 6 | 7 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.06664 | 100 | 1.365 | 100 | 1.692 | 100 | 4.3705 | 97.1225 | 0 | 0 | 0
6 | 6 | 8 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.25133 | 100 | 1.365 | 100 | 1.692 | 100 | 4.1858 | 93.0184 | 0 | 0 | 0
6 | 6 | 9 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.51598 | 100 | 1.365 | 100 | 1.692 | 100 | 3.9212 | 87.1371 | 0 | 0 | 0
6 | 6 | 10 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.78826 | 100 | 1.365 | 100 | 1.692 | 100 | 3.6489 | 81.0866 | 0 | 0 | 0
6 | 6 | 11 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.0034 | 100 | 1.365 | 100 | 1.692 | 100 | 3.4337 | 76.3055 | 0 | 0 | 0
6 | 6 | 12 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.1329 | 100 | 1.365 | 100 | 1.692 | 100 | 3.3043 | 73.4283 | 0 | 0 | 0
6 | 6 | 13 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.1862 | 100 | 1.365 | 100 | 1.692 | 100 | 3.251 | 72.2436 | 0 | 0 | 0
6 | 6 | 14 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.131 | 100 | 1.365 | 100 | 1.692 | 100 | 3.3062 | 73.4706 | 0 | 0 | 0
6 | 6 | 15 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.98627 | 100 | 1.365 | 100 | 1.692 | 100 | 3.4509 | 76.6863 | 0 | 0 | 0
6 | 6 | 16 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.78064 | 100 | 1.365 | 100 | 1.692 | 100 | 3.6565 | 81.2559 | 0 | 0 | 0
6 | 6 | 17 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.5217 | 100 | 1.365 | 100 | 1.692 | 100 | 3.9155 | 87.0102 | 0 | 0 | 0
6 | 6 | 18 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.25704 | 100 | 1.365 | 100 | 1.692 | 100 | 4.1801 | 92.8914 | 0 | 0 | 0
6 | 6 | 19 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.053312 | 100 | 1.365 | 100 | 1.692 | 100 | 4.3838 | 97.4187 | 0 | 0 | 0
6 | 6 | 20 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 6 | 21 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 6 | 22 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 6 | 23 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 6 | 24 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 7 | 1 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 7 | 2 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 7 | 3 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 7 | 4 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 7 | 5 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 7 | 6 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 7 | 7 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.036176 | 100 | 1.365 | 100 | 1.692 | 100 | 4.401 | 97.7995 | 0 | 0 | 0
6 | 7 | 8 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.18659 | 100 | 1.365 | 100 | 1.692 | 100 | 4.2506 | 94.4569 | 0 | 0 | 0
6 | 7 | 9 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.40555 | 100 | 1.365 | 100 | 1.692 | 100 | 4.0316 | 89.5912 | 0 | 0 | 0
6 | 7 | 10 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.64165 | 100 | 1.365 | 100 | 1.692 | 100 | 3.7955 | 84.3446 | 0 | 0 | 0
6 | 7 | 11 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.83966 | 100 | 1.365 | 100 | 1.692 | 100 | 3.5975 | 79.9442 | 0 | 0 | 0
6 | 7 | 12 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.98056 | 100 | 1.365 | 100 | 1.692 | 100 | 3.4566 | 76.8132 | 0 | 0 | 0
6 | 7 | 13 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.032 | 100 | 1.365 | 100 | 1.692 | 100 | 3.4052 | 75.6708 | 0 | 0 | 0
6 | 7 | 14 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.9996 | 100 | 1.365 | 100 | 1.692 | 100 | 3.4376 | 76.3901 | 0 | 0 | 0
6 | 7 | 15 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.88536 | 100 | 1.365 | 100 | 1.692 | 100 | 3.5518 | 78.9288 | 0 | 0 | 0
6 | 7 | 16 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.68925 | 100 | 1.365 | 100 | 1.692 | 100 | 3.7479 | 83.2868 | 0 | 0 | 0
6 | 7 | 17 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.46267 | 100 | 1.365 | 100 | 1.692 | 100 | 3.9745 | 88.3218 | 0 | 0 | 0
6 | 7 | 18 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.2361 | 100 | 1.365 | 100 | 1.692 | 100 | 4.2011 | 93.3568 | 0 | 0 | 0
6 | 7 | 19 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.055216 | 100 | 1.365 | 100 | 1.692 | 100 | 4.3819 | 97.3764 | 0 | 0 | 0
6 | 7 | 20 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 7 | 21 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 7 | 22 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 7 | 23 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 7 | 24 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 8 | 1 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 8 | 2 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 8 | 3 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 8 | 4 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 8 | 5 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 8 | 6 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 8 | 7 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.020944 | 100 | 1.365 | 100 | 1.692 | 100 | 4.4162 | 98.138 | 0 | 0 | 0
6 | 8 | 8 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.1923 | 100 | 1.365 | 100 | 1.692 | 100 | 4.2448 | 94.33 | 0 | 0 | 0
6 | 8 | 9 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.44173 | 100 | 1.365 | 100 | 1.692 | 100 | 3.9954 | 88.7872 | 0 | 0 | 0
6 | 8 | 10 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.69877 | 100 | 1.365 | 100 | 1.692 | 100 | 3.7384 | 83.0752 | 0 | 0 | 0
6 | 8 | 11 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.91392 | 100 | 1.365 | 100 | 1.692 | 100 | 3.5232 | 78.2941 | 0 | 0 | 0
6 | 8 | 12 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.0605 | 100 | 1.365 | 100 | 1.692 | 100 | 3.3766 | 75.0361 | 0 | 0 | 0
6 | 8 | 13 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.1215 | 100 | 1.365 | 100 | 1.692 | 100 | 3.3157 | 73.6822 | 0 | 0 | 0
6 | 8 | 14 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.0681 | 100 | 1.365 | 100 | 1.692 | 100 | 3.369 | 74.8669 | 0 | 0 | 0
6 | 8 | 15 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.94248 | 100 | 1.365 | 100 | 1.692 | 100 | 3.4947 | 77.6594 | 0 | 0 | 0
6 | 8 | 16 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.72923 | 100 | 1.365 | 100 | 1.692 | 100 | 3.7079 | 82.3983 | 0 | 0 | 0
6 | 8 | 17 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.476 | 100 | 1.365 | 100 | 1.692 | 100 | 3.9612 | 88.0256 | 0 | 0 | 0
6 | 8 | 18 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.21896 | 100 | 1.365 | 100 | 1.692 | 100 | 4.2182 | 93.7376 | 0 | 0 | 0
6 | 8 | 19 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.026656 | 100 | 1.365 | 100 | 1.692 | 100 | 4.4105 | 98.0111 | 0 | 0 | 0
6 | 8 | 20 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 8 | 21 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 8 | 22 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 8 | 23 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 8 | 24 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 9 | 1 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 9 | 2 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 9 | 3 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 9 | 4 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 9 | 5 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 9 | 6 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 9 | 7 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.017136 | 100 | 1.365 | 100 | 1.692 | 100 | 4.42 | 98.2226 | 0 | 0 | 0
6 | 9 | 8 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.24752 | 100 | 1.365 | 100 | 1.692 | 100 | 4.1896 | 93.103 | 0 | 0 | 0
6 | 9 | 9 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.59024 | 100 | 1.365 | 100 | 1.692 | 100 | 3.8469 | 85.487 | 0 | 0 | 0
6 | 9 | 10 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.9044 | 100 | 1.365 | 100 | 1.692 | 100 | 3.5328 | 78.5056 | 0 | 0 | 0
6 | 9 | 11 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.1424 | 100 | 1.365 | 100 | 1.692 | 100 | 3.2948 | 73.2168 | 0 | 0 | 0
6 | 9 | 12 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.2909 | 100 | 1.365 | 100 | 1.692 | 100 | 3.1462 | 69.9165 | 0 | 0 | 0
6 | 9 | 13 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.3347 | 100 | 1.365 | 100 | 1.692 | 100 | 3.1024 | 68.9433 | 0 | 0 | 0
6 | 9 | 14 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.2585 | 100 | 1.365 | 100 | 1.692 | 100 | 3.1786 | 70.6358 | 0 | 0 | 0
6 | 9 | 15 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.072 | 100 | 1.365 | 100 | 1.692 | 100 | 3.3652 | 74.7823 | 0 | 0 | 0
6 | 9 | 16 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.82253 | 100 | 1.365 | 100 | 1.692 | 100 | 3.6146 | 80.325 | 0 | 0 | 0
6 | 9 | 17 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.50266 | 100 | 1.365 | 100 | 1.692 | 100 | 3.9345 | 87.4333 | 0 | 0 | 0
6 | 9 | 18 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.16374 | 100 | 1.365 | 100 | 1.692 | 100 | 4.2734 | 94.9647 | 0 | 0 | 0
6 | 9 | 19 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.001904 | 100 | 1.365 | 100 | 1.692 | 100 | 4.4352 | 98.5611 | 0 | 0 | 0
6 | 9 | 20 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 9 | 21 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 9 | 22 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 9 | 23 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 9 | 24 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 10 | 1 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 10 | 2 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 10 | 3 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 10 | 4 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 10 | 5 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 10 | 6 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 10 | 7 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 10 | 8 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.26085 | 100 | 1.365 | 100 | 1.692 | 100 | 4.1763 | 92.8068 | 0 | 0 | 0
6 | 10 | 9 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.69686 | 100 | 1.365 | 100 | 1.692 | 100 | 3.7403 | 83.1176 | 0 | 0 | 0
6 | 10 | 10 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.032 | 100 | 1.365 | 100 | 1.692 | 100 | 3.4052 | 75.6708 | 0 | 0 | 0
6 | 10 | 11 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.2738 | 100 | 1.365 | 100 | 1.692 | 100 | 3.1634 | 70.2973 | 0 | 0 | 0
6 | 10 | 12 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.4128 | 100 | 1.365 | 100 | 1.692 | 100 | 3.0244 | 67.2086 | 0 | 0 | 0
6 | 10 | 13 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.4356 | 100 | 1.365 | 100 | 1.692 | 100 | 3.0015 | 66.7008 | 0 | 0 | 0
6 | 10 | 14 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.3233 | 100 | 1.365 | 100 | 1.692 | 100 | 3.1139 | 69.1972 | 0 | 0 | 0
6 | 10 | 15 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.11 | 100 | 1.365 | 100 | 1.692 | 100 | 3.3271 | 73.936 | 0 | 0 | 0
6 | 10 | 16 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.81301 | 100 | 1.365 | 100 | 1.692 | 100 | 3.6241 | 80.5366 | 0 | 0 | 0
6 | 10 | 17 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.45506 | 100 | 1.365 | 100 | 1.692 | 100 | 3.9821 | 88.4911 | 0 | 0 | 0
6 | 10 | 18 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.059024 | 100 | 1.365 | 100 | 1.692 | 100 | 4.3781 | 97.2918 | 0 | 0 | 0
6 | 10 | 19 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 10 | 20 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 10 | 21 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 10 | 22 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 10 | 23 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 10 | 24 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 11 | 1 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 11 | 2 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 11 | 3 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 11 | 4 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 11 | 5 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 11 | 6 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 11 | 7 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 11 | 8 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.15422 | 100 | 1.365 | 100 | 1.692 | 100 | 4.2829 | 95.1762 | 0 | 0 | 0
6 | 11 | 9 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.62642 | 100 | 1.365 | 100 | 1.692 | 100 | 3.8107 | 84.6831 | 0 | 0 | 0
6 | 11 | 10 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.98056 | 100 | 1.365 | 100 | 1.692 | 100 | 3.4566 | 76.8132 | 0 | 0 | 0
6 | 11 | 11 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.2262 | 100 | 1.365 | 100 | 1.692 | 100 | 3.211 | 71.3551 | 0 | 0 | 0
6 | 11 | 12 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.3614 | 100 | 1.365 | 100 | 1.692 | 100 | 3.0758 | 68.351 | 0 | 0 | 0
6 | 11 | 13 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.3747 | 100 | 1.365 | 100 | 1.692 | 100 | 3.0625 | 68.0548 | 0 | 0 | 0
6 | 11 | 14 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.2795 | 100 | 1.365 | 100 | 1.692 | 100 | 3.1577 | 70.1704 | 0 | 0 | 0
6 | 11 | 15 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.0662 | 100 | 1.365 | 100 | 1.692 | 100 | 3.3709 | 74.9092 | 0 | 0 | 0
6 | 11 | 16 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.76541 | 100 | 1.365 | 100 | 1.692 | 100 | 3.6717 | 81.5944 | 0 | 0 | 0
6 | 11 | 17 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.3332 | 100 | 1.365 | 100 | 1.692 | 100 | 4.104 | 91.199 | 0 | 0 | 0
6 | 11 | 18 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 11 | 19 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 11 | 20 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 11 | 21 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 11 | 22 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 11 | 23 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 11 | 24 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 12 | 1 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 12 | 2 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 12 | 3 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 12 | 4 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 12 | 5 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 12 | 6 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 12 | 7 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 12 | 8 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.062832 | 100 | 1.365 | 100 | 1.692 | 100 | 4.3743 | 97.2072 | 0 | 0 | 0
6 | 12 | 9 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.51979 | 100 | 1.365 | 100 | 1.692 | 100 | 3.9174 | 87.0525 | 0 | 0 | 0
6 | 12 | 10 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.88917 | 100 | 1.365 | 100 | 1.692 | 100 | 3.548 | 78.8441 | 0 | 0 | 0
6 | 12 | 11 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.1538 | 100 | 1.365 | 100 | 1.692 | 100 | 3.2833 | 72.9629 | 0 | 0 | 0
6 | 12 | 12 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.3157 | 100 | 1.365 | 100 | 1.692 | 100 | 3.1215 | 69.3664 | 0 | 0 | 0
6 | 12 | 13 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.3595 | 100 | 1.365 | 100 | 1.692 | 100 | 3.0777 | 68.3933 | 0 | 0 | 0
6 | 12 | 14 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.2776 | 100 | 1.365 | 100 | 1.692 | 100 | 3.1596 | 70.2127 | 0 | 0 | 0
6 | 12 | 15 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 1.0815 | 100 | 1.365 | 100 | 1.692 | 100 | 3.3557 | 74.5707 | 0 | 0 | 0
6 | 12 | 16 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.79778 | 100 | 1.365 | 100 | 1.692 | 100 | 3.6394 | 80.8751 | 0 | 0 | 0
6 | 12 | 17 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.36747 | 100 | 1.365 | 100 | 1.692 | 100 | 4.0697 | 90.4374 | 0 | 0 | 0
6 | 12 | 18 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0.003808 | 100 | 1.365 | 100 | 1.692 | 100 | 4.4333 | 98.5188 | 0 | 0 | 0
6 | 12 | 19 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 12 | 20 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 12 | 21 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 12 | 22 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 12 | 23 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
6 | 12 | 24 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
7 | 1 | 1 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 1 | 2 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 1 | 3 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 1 | 4 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 1 | 5 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 1 | 6 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 1 | 7 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 1 | 8 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.041536 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4542 | 98.9831 | 0 | 0 | 0
7 | 1 | 9 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.45312 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.0427 | 89.8368 | 0 | 0 | 0
7 | 1 | 10 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.83638 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.6594 | 81.3198 | 0 | 0 | 0
7 | 1 | 11 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.1252 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.3705 | 74.9006 | 0 | 0 | 0
7 | 1 | 12 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.3122 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.1836 | 70.747 | 0 | 0 | 0
7 | 1 | 13 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.382 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.1138 | 69.1946 | 0 | 0 | 0
7 | 1 | 14 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.3292 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.1666 | 70.3694 | 0 | 0 | 0
7 | 1 | 15 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.1649 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.3309 | 74.0195 | 0 | 0 | 0
7 | 1 | 16 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.88925 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.6065 | 80.145 | 0 | 0 | 0
7 | 1 | 17 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.53619 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.9596 | 87.9907 | 0 | 0 | 0
7 | 1 | 18 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.07552 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4203 | 98.2279 | 0 | 0 | 0
7 | 1 | 19 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 1 | 20 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 1 | 21 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 1 | 22 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 1 | 23 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 1 | 24 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 2 | 1 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 2 | 2 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 2 | 3 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 2 | 4 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 2 | 5 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 2 | 6 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 2 | 7 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 2 | 8 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.067968 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4278 | 98.3957 | 0 | 0 | 0
7 | 2 | 9 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.49466 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.0011 | 88.9137 | 0 | 0 | 0
7 | 2 | 10 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.87792 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.6179 | 80.3968 | 0 | 0 | 0
7 | 2 | 11 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.1781 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.3177 | 73.7258 | 0 | 0 | 0
7 | 2 | 12 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.3801 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.1156 | 69.2366 | 0 | 0 | 0
7 | 2 | 13 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.4594 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.0364 | 67.4744 | 0 | 0 | 0
7 | 2 | 14 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.4217 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.0741 | 68.3136 | 0 | 0 | 0
7 | 2 | 15 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.265 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.2308 | 71.7959 | 0 | 0 | 0
7 | 2 | 16 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.0044 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.4914 | 77.5857 | 0 | 0 | 0
7 | 2 | 17 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.65514 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.8406 | 85.3475 | 0 | 0 | 0
7 | 2 | 18 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.17181 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.324 | 96.0881 | 0 | 0 | 0
7 | 2 | 19 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 2 | 20 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 2 | 21 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 2 | 22 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 2 | 23 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 2 | 24 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 3 | 1 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 3 | 2 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 3 | 3 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 3 | 4 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 3 | 5 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 3 | 6 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 3 | 7 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.001888 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4939 | 99.8641 | 0 | 0 | 0
7 | 3 | 8 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.1567 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.3391 | 96.4238 | 0 | 0 | 0
7 | 3 | 9 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.56829 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.9275 | 87.2775 | 0 | 0 | 0
7 | 3 | 10 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.93645 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.5593 | 79.0961 | 0 | 0 | 0
7 | 3 | 11 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.2121 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.2837 | 72.9706 | 0 | 0 | 0
7 | 3 | 12 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.4028 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.093 | 68.7331 | 0 | 0 | 0
7 | 3 | 13 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.4745 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.0212 | 67.1388 | 0 | 0 | 0
7 | 3 | 14 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.4405 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.0552 | 67.894 | 0 | 0 | 0
7 | 3 | 15 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.248 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.2478 | 72.1735 | 0 | 0 | 0
7 | 3 | 16 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.98931 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.5065 | 77.9214 | 0 | 0 | 0
7 | 3 | 17 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.64758 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.8482 | 85.5153 | 0 | 0 | 0
7 | 3 | 18 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.24355 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.2522 | 94.4938 | 0 | 0 | 0
7 | 3 | 19 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.001888 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4939 | 99.8641 | 0 | 0 | 0
7 | 3 | 20 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 3 | 21 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 3 | 22 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 3 | 23 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 3 | 24 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 4 | 1 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 4 | 2 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 4 | 3 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 4 | 4 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 4 | 5 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 4 | 6 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 4 | 7 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.02832 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4675 | 99.2768 | 0 | 0 | 0
7 | 4 | 8 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.27376 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.222 | 93.8225 | 0 | 0 | 0
7 | 4 | 9 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.63059 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.8652 | 85.8929 | 0 | 0 | 0
7 | 4 | 10 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.9591 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.5367 | 78.5927 | 0 | 0 | 0
7 | 4 | 11 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.2064 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.2893 | 73.0965 | 0 | 0 | 0
7 | 4 | 12 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.3575 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.1383 | 69.74 | 0 | 0 | 0
7 | 4 | 13 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.4047 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.0911 | 68.6912 | 0 | 0 | 0
7 | 4 | 14 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.3348 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.161 | 70.2435 | 0 | 0 | 0
7 | 4 | 15 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.1668 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.329 | 73.9776 | 0 | 0 | 0
7 | 4 | 16 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.90624 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.5895 | 79.7674 | 0 | 0 | 0
7 | 4 | 17 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.59283 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.9029 | 86.732 | 0 | 0 | 0
7 | 4 | 18 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.24922 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.2466 | 94.368 | 0 | 0 | 0
7 | 4 | 19 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.01888 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4769 | 99.4865 | 0 | 0 | 0
7 | 4 | 20 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 4 | 21 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 4 | 22 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 4 | 23 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 4 | 24 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 5 | 1 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 5 | 2 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 5 | 3 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 5 | 4 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 5 | 5 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 5 | 6 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 5 | 7 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.067968 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4278 | 98.3957 | 0 | 0 | 0
7 | 5 | 8 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.30208 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.1937 | 93.1932 | 0 | 0 | 0
7 | 5 | 9 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.61549 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.8803 | 86.2286 | 0 | 0 | 0
7 | 5 | 10 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.91002 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.5858 | 79.6835 | 0 | 0 | 0
7 | 5 | 11 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.1328 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.363 | 74.7328 | 0 | 0 | 0
7 | 5 | 12 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.2706 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.2252 | 71.67 | 0 | 0 | 0
7 | 5 | 13 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.3084 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.1874 | 70.8309 | 0 | 0 | 0
7 | 5 | 14 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.2423 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.2535 | 72.2993 | 0 | 0 | 0
7 | 5 | 15 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.0837 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.4121 | 75.8236 | 0 | 0 | 0
7 | 5 | 16 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.84394 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.6518 | 81.152 | 0 | 0 | 0
7 | 5 | 17 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.54752 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.9483 | 87.739 | 0 | 0 | 0
7 | 5 | 18 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.25299 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.2428 | 94.284 | 0 | 0 | 0
7 | 5 | 19 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.035872 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4599 | 99.1089 | 0 | 0 | 0
7 | 5 | 20 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 5 | 21 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 5 | 22 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 5 | 23 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 5 | 24 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 6 | 1 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 6 | 2 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 6 | 3 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 6 | 4 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 6 | 5 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 6 | 6 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 6 | 7 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.06608 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4297 | 98.4376 | 0 | 0 | 0
7 | 6 | 8 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.24922 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.2466 | 94.368 | 0 | 0 | 0
7 | 6 | 9 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.51165 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.9841 | 88.5361 | 0 | 0 | 0
7 | 6 | 10 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.78163 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.7141 | 82.5365 | 0 | 0 | 0
7 | 6 | 11 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.99498 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.5008 | 77.7955 | 0 | 0 | 0
7 | 6 | 12 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.1234 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.3724 | 74.9425 | 0 | 0 | 0
7 | 6 | 13 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.1762 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.3196 | 73.7678 | 0 | 0 | 0
7 | 6 | 14 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.1215 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.3743 | 74.9845 | 0 | 0 | 0
7 | 6 | 15 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.97798 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.5178 | 78.1731 | 0 | 0 | 0
7 | 6 | 16 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.77408 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.7217 | 82.7043 | 0 | 0 | 0
7 | 6 | 17 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.51731 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.9785 | 88.4103 | 0 | 0 | 0
7 | 6 | 18 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.25488 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.2409 | 94.2421 | 0 | 0 | 0
7 | 6 | 19 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.052864 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4429 | 98.7313 | 0 | 0 | 0
7 | 6 | 20 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 6 | 21 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 6 | 22 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 6 | 23 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 6 | 24 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 7 | 1 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 7 | 2 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 7 | 3 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 7 | 4 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 7 | 5 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 7 | 6 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 7 | 7 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.035872 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4599 | 99.1089 | 0 | 0 | 0
7 | 7 | 8 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.18502 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.3108 | 95.7944 | 0 | 0 | 0
7 | 7 | 9 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.40214 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.0936 | 90.9696 | 0 | 0 | 0
7 | 7 | 10 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.63626 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.8595 | 85.7671 | 0 | 0 | 0
7 | 7 | 11 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.83261 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.6632 | 81.4037 | 0 | 0 | 0
7 | 7 | 12 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.97232 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.5235 | 78.299 | 0 | 0 | 0
7 | 7 | 13 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.0233 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.4725 | 77.1662 | 0 | 0 | 0
7 | 7 | 14 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.9912 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.5046 | 77.8794 | 0 | 0 | 0
7 | 7 | 15 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.87792 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.6179 | 80.3968 | 0 | 0 | 0
7 | 7 | 16 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.68346 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.8123 | 84.7182 | 0 | 0 | 0
7 | 7 | 17 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.45878 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.037 | 89.7109 | 0 | 0 | 0
7 | 7 | 18 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.23411 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.2617 | 94.7036 | 0 | 0 | 0
7 | 7 | 19 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.054752 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.441 | 98.6894 | 0 | 0 | 0
7 | 7 | 20 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 7 | 21 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 7 | 22 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 7 | 23 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 7 | 24 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 8 | 1 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 8 | 2 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 8 | 3 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 8 | 4 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 8 | 5 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 8 | 6 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 8 | 7 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.020768 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.475 | 99.4446 | 0 | 0 | 0
7 | 8 | 8 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.19069 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.3051 | 95.6686 | 0 | 0 | 0
7 | 8 | 9 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.43802 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.0578 | 90.1724 | 0 | 0 | 0
7 | 8 | 10 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.6929 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.8029 | 84.5084 | 0 | 0 | 0
7 | 8 | 11 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.90624 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.5895 | 79.7674 | 0 | 0 | 0
7 | 8 | 12 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.0516 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.4442 | 76.5368 | 0 | 0 | 0
7 | 8 | 13 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.112 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.3837 | 75.1943 | 0 | 0 | 0
7 | 8 | 14 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.0592 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.4366 | 76.369 | 0 | 0 | 0
7 | 8 | 15 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.93456 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.5612 | 79.1381 | 0 | 0 | 0
7 | 8 | 16 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.7231 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.7727 | 83.8371 | 0 | 0 | 0
7 | 8 | 17 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.472 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.0238 | 89.4172 | 0 | 0 | 0
7 | 8 | 18 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.21712 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.2787 | 95.0812 | 0 | 0 | 0
7 | 8 | 19 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.026432 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4693 | 99.3187 | 0 | 0 | 0
7 | 8 | 20 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 8 | 21 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 8 | 22 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 8 | 23 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 8 | 24 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 9 | 1 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 9 | 2 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 9 | 3 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 9 | 4 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 9 | 5 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 9 | 6 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 9 | 7 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.016992 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4788 | 99.5285 | 0 | 0 | 0
7 | 9 | 8 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.24544 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.2503 | 94.4519 | 0 | 0 | 0
7 | 9 | 9 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.58528 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.9105 | 86.8999 | 0 | 0 | 0
7 | 9 | 10 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.8968 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.599 | 79.9772 | 0 | 0 | 0
7 | 9 | 11 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.1328 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.363 | 74.7328 | 0 | 0 | 0
7 | 9 | 12 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.2801 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.2157 | 71.4602 | 0 | 0 | 0
7 | 9 | 13 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.3235 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.1723 | 70.4952 | 0 | 0 | 0
7 | 9 | 14 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.248 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.2478 | 72.1735 | 0 | 0 | 0
7 | 9 | 15 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.0629 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.4328 | 76.2851 | 0 | 0 | 0
7 | 9 | 16 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.81562 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.6802 | 81.7813 | 0 | 0 | 0
7 | 9 | 17 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.49843 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.9973 | 88.8298 | 0 | 0 | 0
7 | 9 | 18 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.16237 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.3334 | 96.2979 | 0 | 0 | 0
7 | 9 | 19 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.001888 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4939 | 99.8641 | 0 | 0 | 0
7 | 9 | 20 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 9 | 21 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 9 | 22 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 9 | 23 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 9 | 24 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 10 | 1 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 10 | 2 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 10 | 3 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 10 | 4 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 10 | 5 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 10 | 6 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 10 | 7 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 10 | 8 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.25866 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.2371 | 94.1582 | 0 | 0 | 0
7 | 10 | 9 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.69101 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.8048 | 84.5504 | 0 | 0 | 0
7 | 10 | 10 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.0233 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.4725 | 77.1662 | 0 | 0 | 0
7 | 10 | 11 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.2631 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.2327 | 71.8378 | 0 | 0 | 0
7 | 10 | 12 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.4009 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.0949 | 68.7751 | 0 | 0 | 0
7 | 10 | 13 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.4236 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.0722 | 68.2716 | 0 | 0 | 0
7 | 10 | 14 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.3122 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.1836 | 70.747 | 0 | 0 | 0
7 | 10 | 15 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.1007 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.3951 | 75.446 | 0 | 0 | 0
7 | 10 | 16 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.80618 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.6896 | 81.9911 | 0 | 0 | 0
7 | 10 | 17 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.45123 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.0445 | 89.8787 | 0 | 0 | 0
7 | 10 | 18 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.058528 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4372 | 98.6055 | 0 | 0 | 0
7 | 10 | 19 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 10 | 20 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 10 | 21 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 10 | 22 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 10 | 23 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 10 | 24 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 11 | 1 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 11 | 2 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 11 | 3 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 11 | 4 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 11 | 5 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 11 | 6 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 11 | 7 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 11 | 8 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.15293 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.3428 | 96.5077 | 0 | 0 | 0
7 | 11 | 9 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.62115 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.8746 | 86.1027 | 0 | 0 | 0
7 | 11 | 10 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.97232 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.5235 | 78.299 | 0 | 0 | 0
7 | 11 | 11 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.2159 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.2799 | 72.8867 | 0 | 0 | 0
7 | 11 | 12 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.3499 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.1459 | 69.9079 | 0 | 0 | 0
7 | 11 | 13 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.3631 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.1326 | 69.6142 | 0 | 0 | 0
7 | 11 | 14 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.2687 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.227 | 71.712 | 0 | 0 | 0
7 | 11 | 15 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.0573 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.4385 | 76.411 | 0 | 0 | 0
7 | 11 | 16 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.75898 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.7368 | 83.04 | 0 | 0 | 0
7 | 11 | 17 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.3304 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.1654 | 92.5639 | 0 | 0 | 0
7 | 11 | 18 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 11 | 19 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 11 | 20 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 11 | 21 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 11 | 22 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 11 | 23 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 11 | 24 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 12 | 1 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 12 | 2 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 12 | 3 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 12 | 4 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 12 | 5 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 12 | 6 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 12 | 7 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 12 | 8 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.062304 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.4335 | 98.5216 | 0 | 0 | 0
7 | 12 | 9 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.51542 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.9804 | 88.4522 | 0 | 0 | 0
7 | 12 | 10 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.8817 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.6141 | 80.3128 | 0 | 0 | 0
7 | 12 | 11 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.1441 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.3516 | 74.481 | 0 | 0 | 0
7 | 12 | 12 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.3046 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.1912 | 70.9148 | 0 | 0 | 0
7 | 12 | 13 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.348 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.1477 | 69.9498 | 0 | 0 | 0
7 | 12 | 14 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.2668 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.2289 | 71.7539 | 0 | 0 | 0
7 | 12 | 15 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 1.0724 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.4234 | 76.0753 | 0 | 0 | 0
7 | 12 | 16 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.79107 | 100 | 1.3425 | 100 | 1.665 | 100 | 3.7047 | 82.3267 | 0 | 0 | 0
7 | 12 | 17 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.36438 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.1314 | 91.8087 | 0 | 0 | 0
7 | 12 | 18 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.003776 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.492 | 99.8222 | 0 | 0 | 0
7 | 12 | 19 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 12 | 20 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 12 | 21 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 12 | 22 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 12 | 23 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
7 | 12 | 24 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0 | 0 | 1.3425 | 100 | 1.665 | 100 | 4.4958 | 99.9061 | 0 | 0 | 0
8 | 1 | 1 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 1 | 2 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 1 | 3 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 1 | 4 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 1 | 5 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 1 | 6 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 1 | 7 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 1 | 8 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.041184 | 100 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.01321 | 0.58247 | 0
8 | 1 | 9 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.44928 | 100 | 1.32 | 100 | 1.638 | 100 | 4.1051 | 91.2248 | 0 | 0 | 0
8 | 1 | 10 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.8293 | 100 | 1.32 | 100 | 1.638 | 100 | 3.7251 | 82.78 | 0 | 0 | 0
8 | 1 | 11 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.1157 | 100 | 1.32 | 100 | 1.638 | 100 | 3.4387 | 76.4152 | 0 | 0 | 0
8 | 1 | 12 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.301 | 100 | 1.32 | 100 | 1.638 | 100 | 3.2534 | 72.2968 | 0 | 0 | 0
8 | 1 | 13 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.3703 | 100 | 1.32 | 100 | 1.638 | 100 | 3.1841 | 70.7576 | 0 | 0 | 0
8 | 1 | 14 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.3179 | 100 | 1.32 | 100 | 1.638 | 100 | 3.2365 | 71.9224 | 0 | 0 | 0
8 | 1 | 15 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.155 | 100 | 1.32 | 100 | 1.638 | 100 | 3.3994 | 75.5416 | 0 | 0 | 0
8 | 1 | 16 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.88171 | 100 | 1.32 | 100 | 1.638 | 100 | 3.6727 | 81.6152 | 0 | 0 | 0
8 | 1 | 17 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.53165 | 100 | 1.32 | 100 | 1.638 | 100 | 4.0227 | 89.3944 | 0 | 0 | 0
8 | 1 | 18 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.07488 | 100 | 1.32 | 100 | 1.638 | 100 | 4.4795 | 99.5448 | 0 | 0 | 0
8 | 1 | 19 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 1 | 20 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 1 | 21 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 1 | 22 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 1 | 23 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 1 | 24 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 2 | 1 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 2 | 2 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 2 | 3 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 2 | 4 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 2 | 5 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 2 | 6 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 2 | 7 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 2 | 8 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.067392 | 100 | 1.32 | 100 | 1.638 | 100 | 4.487 | 99.7112 | 0 | 0 | 0
8 | 2 | 9 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.49046 | 100 | 1.32 | 100 | 1.638 | 100 | 4.0639 | 90.3096 | 0 | 0 | 0
8 | 2 | 10 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.87048 | 100 | 1.32 | 100 | 1.638 | 100 | 3.6839 | 81.8648 | 0 | 0 | 0
8 | 2 | 11 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.1681 | 100 | 1.32 | 100 | 1.638 | 100 | 3.3863 | 75.2504 | 0 | 0 | 0
8 | 2 | 12 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.3684 | 100 | 1.32 | 100 | 1.638 | 100 | 3.186 | 70.7992 | 0 | 0 | 0
8 | 2 | 13 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.4471 | 100 | 1.32 | 100 | 1.638 | 100 | 3.1073 | 69.052 | 0 | 0 | 0
8 | 2 | 14 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.4096 | 100 | 1.32 | 100 | 1.638 | 100 | 3.1448 | 69.884 | 0 | 0 | 0
8 | 2 | 15 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.2542 | 100 | 1.32 | 100 | 1.638 | 100 | 3.3002 | 73.3368 | 0 | 0 | 0
8 | 2 | 16 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.9959 | 100 | 1.32 | 100 | 1.638 | 100 | 3.5585 | 79.0776 | 0 | 0 | 0
8 | 2 | 17 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.64958 | 100 | 1.32 | 100 | 1.638 | 100 | 3.9048 | 86.7736 | 0 | 0 | 0
8 | 2 | 18 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.17035 | 100 | 1.32 | 100 | 1.638 | 100 | 4.384 | 97.4232 | 0 | 0 | 0
8 | 2 | 19 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 2 | 20 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 2 | 21 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 2 | 22 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 2 | 23 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 2 | 24 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 3 | 1 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 3 | 2 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 3 | 3 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 3 | 4 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 3 | 5 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 3 | 6 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 3 | 7 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.001872 | 100 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.052522 | 2.3158 | 0
8 | 3 | 8 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.15538 | 100 | 1.32 | 100 | 1.638 | 100 | 4.399 | 97.756 | 0 | 0 | 0
8 | 3 | 9 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.56347 | 100 | 1.32 | 100 | 1.638 | 100 | 3.9909 | 88.6872 | 0 | 0 | 0
8 | 3 | 10 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.92851 | 100 | 1.32 | 100 | 1.638 | 100 | 3.6259 | 80.5752 | 0 | 0 | 0
8 | 3 | 11 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.2018 | 100 | 1.32 | 100 | 1.638 | 100 | 3.3526 | 74.5016 | 0 | 0 | 0
8 | 3 | 12 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.3909 | 100 | 1.32 | 100 | 1.638 | 100 | 3.1635 | 70.3 | 0 | 0 | 0
8 | 3 | 13 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.462 | 100 | 1.32 | 100 | 1.638 | 100 | 3.0924 | 68.7192 | 0 | 0 | 0
8 | 3 | 14 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.4283 | 100 | 1.32 | 100 | 1.638 | 100 | 3.1261 | 69.468 | 0 | 0 | 0
8 | 3 | 15 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.2374 | 100 | 1.32 | 100 | 1.638 | 100 | 3.317 | 73.7112 | 0 | 0 | 0
8 | 3 | 16 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.98093 | 100 | 1.32 | 100 | 1.638 | 100 | 3.5735 | 79.4104 | 0 | 0 | 0
8 | 3 | 17 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.6421 | 100 | 1.32 | 100 | 1.638 | 100 | 3.9123 | 86.94 | 0 | 0 | 0
8 | 3 | 18 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.24149 | 100 | 1.32 | 100 | 1.638 | 100 | 4.3129 | 95.8424 | 0 | 0 | 0
8 | 3 | 19 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.001872 | 100 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.052522 | 2.3158 | 0
8 | 3 | 20 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 3 | 21 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 3 | 22 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 3 | 23 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 3 | 24 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 4 | 1 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 4 | 2 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 4 | 3 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 4 | 4 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 4 | 5 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 4 | 6 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 4 | 7 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.02808 | 100 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.026314 | 1.1602 | 0
8 | 4 | 8 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.27144 | 100 | 1.32 | 100 | 1.638 | 100 | 4.283 | 95.1768 | 0 | 0 | 0
8 | 4 | 9 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.62525 | 100 | 1.32 | 100 | 1.638 | 100 | 3.9291 | 87.3144 | 0 | 0 | 0
8 | 4 | 10 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.95098 | 100 | 1.32 | 100 | 1.638 | 100 | 3.6034 | 80.076 | 0 | 0 | 0
8 | 4 | 11 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.1962 | 100 | 1.32 | 100 | 1.638 | 100 | 3.3582 | 74.6264 | 0 | 0 | 0
8 | 4 | 12 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.346 | 100 | 1.32 | 100 | 1.638 | 100 | 3.2084 | 71.2984 | 0 | 0 | 0
8 | 4 | 13 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.3928 | 100 | 1.32 | 100 | 1.638 | 100 | 3.1616 | 70.2584 | 0 | 0 | 0
8 | 4 | 14 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.3235 | 100 | 1.32 | 100 | 1.638 | 100 | 3.2309 | 71.7976 | 0 | 0 | 0
8 | 4 | 15 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.1569 | 100 | 1.32 | 100 | 1.638 | 100 | 3.3975 | 75.5 | 0 | 0 | 0
8 | 4 | 16 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.89856 | 100 | 1.32 | 100 | 1.638 | 100 | 3.6558 | 81.2408 | 0 | 0 | 0
8 | 4 | 17 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.58781 | 100 | 1.32 | 100 | 1.638 | 100 | 3.9666 | 88.1464 | 0 | 0 | 0
8 | 4 | 18 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.2471 | 100 | 1.32 | 100 | 1.638 | 100 | 4.3073 | 95.7176 | 0 | 0 | 0
8 | 4 | 19 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.01872 | 100 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.035674 | 1.5729 | 0
8 | 4 | 20 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 4 | 21 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 4 | 22 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 4 | 23 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 4 | 24 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 5 | 1 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 5 | 2 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 5 | 3 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 5 | 4 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 5 | 5 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 5 | 6 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 5 | 7 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.067392 | 100 | 1.32 | 100 | 1.638 | 100 | 4.487 | 99.7112 | 0 | 0 | 0
8 | 5 | 8 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.29952 | 100 | 1.32 | 100 | 1.638 | 100 | 4.2549 | 94.5528 | 0 | 0 | 0
8 | 5 | 9 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.61027 | 100 | 1.32 | 100 | 1.638 | 100 | 3.9441 | 87.6472 | 0 | 0 | 0
8 | 5 | 10 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.9023 | 100 | 1.32 | 100 | 1.638 | 100 | 3.6521 | 81.1576 | 0 | 0 | 0
8 | 5 | 11 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.1232 | 100 | 1.32 | 100 | 1.638 | 100 | 3.4312 | 76.2488 | 0 | 0 | 0
8 | 5 | 12 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.2599 | 100 | 1.32 | 100 | 1.638 | 100 | 3.2945 | 73.212 | 0 | 0 | 0
8 | 5 | 13 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.2973 | 100 | 1.32 | 100 | 1.638 | 100 | 3.2571 | 72.38 | 0 | 0 | 0
8 | 5 | 14 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.2318 | 100 | 1.32 | 100 | 1.638 | 100 | 3.3226 | 73.836 | 0 | 0 | 0
8 | 5 | 15 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.0745 | 100 | 1.32 | 100 | 1.638 | 100 | 3.4799 | 77.3304 | 0 | 0 | 0
8 | 5 | 16 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.83678 | 100 | 1.32 | 100 | 1.638 | 100 | 3.7176 | 82.6136 | 0 | 0 | 0
8 | 5 | 17 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.54288 | 100 | 1.32 | 100 | 1.638 | 100 | 4.0115 | 89.1448 | 0 | 0 | 0
8 | 5 | 18 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.25085 | 100 | 1.32 | 100 | 1.638 | 100 | 4.3035 | 95.6344 | 0 | 0 | 0
8 | 5 | 19 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.035568 | 100 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.018826 | 0.83009 | 0
8 | 5 | 20 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 5 | 21 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 5 | 22 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 5 | 23 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 5 | 24 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 6 | 1 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 6 | 2 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 6 | 3 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 6 | 4 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 6 | 5 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 6 | 6 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 6 | 7 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.06552 | 100 | 1.32 | 100 | 1.638 | 100 | 4.4889 | 99.7528 | 0 | 0 | 0
8 | 6 | 8 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.2471 | 100 | 1.32 | 100 | 1.638 | 100 | 4.3073 | 95.7176 | 0 | 0 | 0
8 | 6 | 9 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.50731 | 100 | 1.32 | 100 | 1.638 | 100 | 4.0471 | 89.9352 | 0 | 0 | 0
8 | 6 | 10 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.77501 | 100 | 1.32 | 100 | 1.638 | 100 | 3.7794 | 83.9864 | 0 | 0 | 0
8 | 6 | 11 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.98654 | 100 | 1.32 | 100 | 1.638 | 100 | 3.5679 | 79.2856 | 0 | 0 | 0
8 | 6 | 12 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.1138 | 100 | 1.32 | 100 | 1.638 | 100 | 3.4406 | 76.4568 | 0 | 0 | 0
8 | 6 | 13 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.1663 | 100 | 1.32 | 100 | 1.638 | 100 | 3.3881 | 75.292 | 0 | 0 | 0
8 | 6 | 14 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.112 | 100 | 1.32 | 100 | 1.638 | 100 | 3.4424 | 76.4984 | 0 | 0 | 0
8 | 6 | 15 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.9697 | 100 | 1.32 | 100 | 1.638 | 100 | 3.5847 | 79.66 | 0 | 0 | 0
8 | 6 | 16 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.76752 | 100 | 1.32 | 100 | 1.638 | 100 | 3.7869 | 84.1528 | 0 | 0 | 0
8 | 6 | 17 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.51293 | 100 | 1.32 | 100 | 1.638 | 100 | 4.0415 | 89.8104 | 0 | 0 | 0
8 | 6 | 18 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.25272 | 100 | 1.32 | 100 | 1.638 | 100 | 4.3017 | 95.5928 | 0 | 0 | 0
8 | 6 | 19 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.052416 | 100 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.0019784 | 0.087232 | 0
8 | 6 | 20 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 6 | 21 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 6 | 22 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 6 | 23 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 6 | 24 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 7 | 1 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 7 | 2 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 7 | 3 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 7 | 4 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 7 | 5 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 7 | 6 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 7 | 7 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.035568 | 100 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.018826 | 0.83009 | 0
8 | 7 | 8 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.18346 | 100 | 1.32 | 100 | 1.638 | 100 | 4.3709 | 97.132 | 0 | 0 | 0
8 | 7 | 9 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.39874 | 100 | 1.32 | 100 | 1.638 | 100 | 4.1557 | 92.348 | 0 | 0 | 0
8 | 7 | 10 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.63086 | 100 | 1.32 | 100 | 1.638 | 100 | 3.9235 | 87.1896 | 0 | 0 | 0
8 | 7 | 11 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.82555 | 100 | 1.32 | 100 | 1.638 | 100 | 3.7288 | 82.8632 | 0 | 0 | 0
8 | 7 | 12 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.96408 | 100 | 1.32 | 100 | 1.638 | 100 | 3.5903 | 79.7848 | 0 | 0 | 0
8 | 7 | 13 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.0146 | 100 | 1.32 | 100 | 1.638 | 100 | 3.5398 | 78.6616 | 0 | 0 | 0
8 | 7 | 14 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.9828 | 100 | 1.32 | 100 | 1.638 | 100 | 3.5716 | 79.3688 | 0 | 0 | 0
8 | 7 | 15 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.87048 | 100 | 1.32 | 100 | 1.638 | 100 | 3.6839 | 81.8648 | 0 | 0 | 0
8 | 7 | 16 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.67766 | 100 | 1.32 | 100 | 1.638 | 100 | 3.8767 | 86.1496 | 0 | 0 | 0
8 | 7 | 17 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.4549 | 100 | 1.32 | 100 | 1.638 | 100 | 4.0995 | 91.1 | 0 | 0 | 0
8 | 7 | 18 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.23213 | 100 | 1.32 | 100 | 1.638 | 100 | 4.3223 | 96.0504 | 0 | 0 | 0
8 | 7 | 19 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.054288 | 100 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.00010642 | 0.0046921 | 0
8 | 7 | 20 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 7 | 21 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 7 | 22 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 7 | 23 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 7 | 24 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 8 | 1 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 8 | 2 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 8 | 3 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 8 | 4 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 8 | 5 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 8 | 6 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 8 | 7 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.020592 | 100 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.033802 | 1.4904 | 0
8 | 8 | 8 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.18907 | 100 | 1.32 | 100 | 1.638 | 100 | 4.3653 | 97.0072 | 0 | 0 | 0
8 | 8 | 9 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.4343 | 100 | 1.32 | 100 | 1.638 | 100 | 4.1201 | 91.5576 | 0 | 0 | 0
8 | 8 | 10 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.68702 | 100 | 1.32 | 100 | 1.638 | 100 | 3.8674 | 85.9416 | 0 | 0 | 0
8 | 8 | 11 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.89856 | 100 | 1.32 | 100 | 1.638 | 100 | 3.6558 | 81.2408 | 0 | 0 | 0
8 | 8 | 12 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.0427 | 100 | 1.32 | 100 | 1.638 | 100 | 3.5117 | 78.0376 | 0 | 0 | 0
8 | 8 | 13 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.1026 | 100 | 1.32 | 100 | 1.638 | 100 | 3.4518 | 76.7064 | 0 | 0 | 0
8 | 8 | 14 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.0502 | 100 | 1.32 | 100 | 1.638 | 100 | 3.5042 | 77.8712 | 0 | 0 | 0
8 | 8 | 15 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.92664 | 100 | 1.32 | 100 | 1.638 | 100 | 3.6278 | 80.6168 | 0 | 0 | 0
8 | 8 | 16 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.71698 | 100 | 1.32 | 100 | 1.638 | 100 | 3.8374 | 85.276 | 0 | 0 | 0
8 | 8 | 17 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.468 | 100 | 1.32 | 100 | 1.638 | 100 | 4.0864 | 90.8088 | 0 | 0 | 0
8 | 8 | 18 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.21528 | 100 | 1.32 | 100 | 1.638 | 100 | 4.3391 | 96.4248 | 0 | 0 | 0
8 | 8 | 19 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.026208 | 100 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.028186 | 1.2428 | 0
8 | 8 | 20 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 8 | 21 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 8 | 22 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 8 | 23 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 8 | 24 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 9 | 1 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 9 | 2 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 9 | 3 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 9 | 4 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 9 | 5 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 9 | 6 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 9 | 7 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.016848 | 100 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.037546 | 1.6555 | 0
8 | 9 | 8 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.24336 | 100 | 1.32 | 100 | 1.638 | 100 | 4.311 | 95.8008 | 0 | 0 | 0
8 | 9 | 9 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.58032 | 100 | 1.32 | 100 | 1.638 | 100 | 3.9741 | 88.3128 | 0 | 0 | 0
8 | 9 | 10 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.8892 | 100 | 1.32 | 100 | 1.638 | 100 | 3.6652 | 81.4488 | 0 | 0 | 0
8 | 9 | 11 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.1232 | 100 | 1.32 | 100 | 1.638 | 100 | 3.4312 | 76.2488 | 0 | 0 | 0
8 | 9 | 12 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.2692 | 100 | 1.32 | 100 | 1.638 | 100 | 3.2852 | 73.004 | 0 | 0 | 0
8 | 9 | 13 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.3123 | 100 | 1.32 | 100 | 1.638 | 100 | 3.2421 | 72.0472 | 0 | 0 | 0
8 | 9 | 14 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.2374 | 100 | 1.32 | 100 | 1.638 | 100 | 3.317 | 73.7112 | 0 | 0 | 0
8 | 9 | 15 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.0539 | 100 | 1.32 | 100 | 1.638 | 100 | 3.5005 | 77.788 | 0 | 0 | 0
8 | 9 | 16 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.8087 | 100 | 1.32 | 100 | 1.638 | 100 | 3.7457 | 83.2376 | 0 | 0 | 0
8 | 9 | 17 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.49421 | 100 | 1.32 | 100 | 1.638 | 100 | 4.0602 | 90.2264 | 0 | 0 | 0
8 | 9 | 18 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.16099 | 100 | 1.32 | 100 | 1.638 | 100 | 4.3934 | 97.6312 | 0 | 0 | 0
8 | 9 | 19 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.001872 | 100 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.052522 | 2.3158 | 0
8 | 9 | 20 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 9 | 21 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 9 | 22 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 9 | 23 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 9 | 24 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 10 | 1 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 10 | 2 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 10 | 3 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 10 | 4 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 10 | 5 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 10 | 6 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 10 | 7 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 10 | 8 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.25646 | 100 | 1.32 | 100 | 1.638 | 100 | 4.2979 | 95.5096 | 0 | 0 | 0
8 | 10 | 9 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.68515 | 100 | 1.32 | 100 | 1.638 | 100 | 3.8692 | 85.9832 | 0 | 0 | 0
8 | 10 | 10 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.0146 | 100 | 1.32 | 100 | 1.638 | 100 | 3.5398 | 78.6616 | 0 | 0 | 0
8 | 10 | 11 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.2524 | 100 | 1.32 | 100 | 1.638 | 100 | 3.302 | 73.3784 | 0 | 0 | 0
8 | 10 | 12 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.389 | 100 | 1.32 | 100 | 1.638 | 100 | 3.1654 | 70.3416 | 0 | 0 | 0
8 | 10 | 13 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.4115 | 100 | 1.32 | 100 | 1.638 | 100 | 3.1429 | 69.8424 | 0 | 0 | 0
8 | 10 | 14 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.301 | 100 | 1.32 | 100 | 1.638 | 100 | 3.2534 | 72.2968 | 0 | 0 | 0
8 | 10 | 15 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.0914 | 100 | 1.32 | 100 | 1.638 | 100 | 3.463 | 76.956 | 0 | 0 | 0
8 | 10 | 16 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.79934 | 100 | 1.32 | 100 | 1.638 | 100 | 3.7551 | 83.4456 | 0 | 0 | 0
8 | 10 | 17 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.44741 | 100 | 1.32 | 100 | 1.638 | 100 | 4.107 | 91.2664 | 0 | 0 | 0
8 | 10 | 18 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.058032 | 100 | 1.32 | 100 | 1.638 | 100 | 4.4964 | 99.9192 | 0 | 0 | 0
8 | 10 | 19 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 10 | 20 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 10 | 21 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 10 | 22 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 10 | 23 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 10 | 24 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 11 | 1 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 11 | 2 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 11 | 3 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 11 | 4 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 11 | 5 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 11 | 6 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 11 | 7 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 11 | 8 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.15163 | 100 | 1.32 | 100 | 1.638 | 100 | 4.4028 | 97.8392 | 0 | 0 | 0
8 | 11 | 9 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.61589 | 100 | 1.32 | 100 | 1.638 | 100 | 3.9385 | 87.5224 | 0 | 0 | 0
8 | 11 | 10 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.96408 | 100 | 1.32 | 100 | 1.638 | 100 | 3.5903 | 79.7848 | 0 | 0 | 0
8 | 11 | 11 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.2056 | 100 | 1.32 | 100 | 1.638 | 100 | 3.3488 | 74.4184 | 0 | 0 | 0
8 | 11 | 12 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.3385 | 100 | 1.32 | 100 | 1.638 | 100 | 3.2159 | 71.4648 | 0 | 0 | 0
8 | 11 | 13 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.3516 | 100 | 1.32 | 100 | 1.638 | 100 | 3.2028 | 71.1736 | 0 | 0 | 0
8 | 11 | 14 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.258 | 100 | 1.32 | 100 | 1.638 | 100 | 3.2964 | 73.2536 | 0 | 0 | 0
8 | 11 | 15 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.0483 | 100 | 1.32 | 100 | 1.638 | 100 | 3.5061 | 77.9128 | 0 | 0 | 0
8 | 11 | 16 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.75254 | 100 | 1.32 | 100 | 1.638 | 100 | 3.8019 | 84.4856 | 0 | 0 | 0
8 | 11 | 17 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.3276 | 100 | 1.32 | 100 | 1.638 | 100 | 4.2268 | 93.9288 | 0 | 0 | 0
8 | 11 | 18 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 11 | 19 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 11 | 20 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 11 | 21 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 11 | 22 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 11 | 23 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 11 | 24 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 12 | 1 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 12 | 2 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 12 | 3 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 12 | 4 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 12 | 5 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 12 | 6 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 12 | 7 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 12 | 8 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.061776 | 100 | 1.32 | 100 | 1.638 | 100 | 4.4926 | 99.836 | 0 | 0 | 0
8 | 12 | 9 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.51106 | 100 | 1.32 | 100 | 1.638 | 100 | 4.0433 | 89.852 | 0 | 0 | 0
8 | 12 | 10 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.87422 | 100 | 1.32 | 100 | 1.638 | 100 | 3.6802 | 81.7816 | 0 | 0 | 0
8 | 12 | 11 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.1344 | 100 | 1.32 | 100 | 1.638 | 100 | 3.42 | 75.9992 | 0 | 0 | 0
8 | 12 | 12 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.2936 | 100 | 1.32 | 100 | 1.638 | 100 | 3.2608 | 72.4632 | 0 | 0 | 0
8 | 12 | 13 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.3366 | 100 | 1.32 | 100 | 1.638 | 100 | 3.2178 | 71.5064 | 0 | 0 | 0
8 | 12 | 14 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.2561 | 100 | 1.32 | 100 | 1.638 | 100 | 3.2983 | 73.2952 | 0 | 0 | 0
8 | 12 | 15 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 1.0633 | 100 | 1.32 | 100 | 1.638 | 100 | 3.4911 | 77.58 | 0 | 0 | 0
8 | 12 | 16 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.78437 | 100 | 1.32 | 100 | 1.638 | 100 | 3.77 | 83.7784 | 0 | 0 | 0
8 | 12 | 17 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.3613 | 100 | 1.32 | 100 | 1.638 | 100 | 4.1931 | 93.18 | 0 | 0 | 0
8 | 12 | 18 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0.003744 | 100 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.05065 | 2.2333 | 0
8 | 12 | 19 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 12 | 20 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 12 | 21 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 12 | 22 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 12 | 23 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0
8 | 12 | 24 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0

## energy
year | month | Prod Energy Req, MWh | Cooling Energy Req, MWh | Cooling Energy Req after CHP adj., MWh | BESS Charging Energy Req, MWh | Total Energy Req, MWh | Solar Output in MWh | Remaining Energy Demand (after Renewables) MWh | Gas Generator Potential Failures | Gas Generator Failures mitigated | Gas Generator Unavailability, hrs | Gas Generator Output in MWh | Existing Gas Generators Potential Failures | Existing Gas Generators Failures mitigated | Existing Gas Generators Unavailability, hrs | Existing Gas Generators Output in MWh | Grid Potential Failures | Grid Failures mitigated | Grid Unavailability, hrs | Grid Peak Energy, MWh | Grid Off Peak Energy, MWh | Diesel Generator Output in MWh | Final Unserved Energy Req in MWh
1 | 1 | 1391.6667 | 202.895 | 0.35854 | 7.5 | 1399.5252 | 300.8736 | 1098.6516 | 1 | 1 | 0 | 1032.7725 | 1 | 1 | 0 | 0 | 4 | 4 | 0 | 22.6698 | 88.2093 | 0 | 0
1 | 2 | 1410.7143 | 199.92 | 16.9838 | 6 | 1433.6981 | 293.632 | 1140.0661 | 0 | 0 | 0 | 992.88 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 27.6198 | 119.5663 | 14.68 | 0
1 | 3 | 1259.5238 | 442.68 | 240.1435 | 7.5 | 1507.1674 | 336.1888 | 1170.9786 | 0 | 0 | 0 | 1099.26 | 1 | 1 | 0 | 0 | 5 | 5 | 0 | 20.3366 | 96.382 | 18.35 | 0
1 | 4 | 1394.0476 | 428.4 | 232.397 | 7.5 | 1633.9446 | 319.3248 | 1314.6198 | 1 | 1 | 0 | 997.3125 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 62.384 | 299.9233 | 0 | 0
1 | 5 | 1260.7143 | 442.68 | 240.1435 | 7.5 | 1508.3578 | 313.2736 | 1195.0842 | 0 | 0 | 0 | 1099.26 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 16.0372 | 79.787 | 18.35 | 0
1 | 6 | 1282.1429 | 428.4 | 232.397 | 7.5 | 1522.0398 | 271.1136 | 1250.9262 | 1 | 1 | 0 | 997.3125 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 55.0463 | 243.5675 | 0 | 0
1 | 7 | 1309.5238 | 442.68 | 240.1435 | 7.5 | 1557.1674 | 240.7584 | 1316.409 | 0 | 0 | 0 | 1099.26 | 1 | 1 | 0 | 0 | 3 | 3 | 0 | 47.2728 | 214.8762 | 11.01 | 0
1 | 8 | 1258.3333 | 442.68 | 240.1435 | 7.5 | 1505.9769 | 255.6384 | 1250.3385 | 0 | 0 | 0 | 1099.26 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 27.4463 | 123.6321 | 14.68 | 0
1 | 9 | 1352.381 | 428.4 | 232.397 | 7.5 | 1592.2779 | 292.3424 | 1299.9355 | 1 | 1 | 0 | 997.3125 | 1 | 1 | 0 | 0 | 4 | 4 | 0 | 66.602 | 281.021 | 0 | 0
1 | 10 | 1366.6667 | 442.68 | 240.1435 | 7.5 | 1614.3102 | 318.8288 | 1295.4814 | 0 | 0 | 0 | 1099.26 | 1 | 1 | 0 | 0 | 5 | 5 | 0 | 44.787 | 196.4344 | 18.35 | 0
1 | 11 | 1279.7619 | 178.5 | 0 | 7.5 | 1287.2619 | 286.5888 | 1000.6731 | 0 | 0 | 0 | 1000.6731 | 1 | 1 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0
1 | 12 | 1428.5714 | 184.45 | 0 | 7.5 | 1436.0714 | 285.1008 | 1150.9706 | 1 | 1 | 0 | 1032.7725 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 32.1153 | 131.0828 | 0 | 0
2 | 1 | 1391.6667 | 202.895 | 3.4429 | 7.5 | 1402.6095 | 298.4472 | 1104.1623 | 1 | 1 | 0 | 1017.045 | 0 | 0 | 0 | 132.1173 | 2 | 2 | 0 | 0 | 0 | 0 | 0
2 | 2 | 1410.7143 | 199.92 | 19.7697 | 6 | 1436.484 | 291.264 | 1145.22 | 1 | 1 | 0 | 912.285 | 0 | 0 | 0 | 277.935 | 3 | 3 | 0 | 0 | 0 | 0 | 0
2 | 3 | 1259.5238 | 442.68 | 243.2279 | 7.5 | 1510.2517 | 333.4776 | 1176.7741 | 1 | 1 | 0 | 1017.045 | 0 | 0 | 0 | 204.7291 | 3 | 3 | 0 | 0 | 0 | 0 | 0
2 | 4 | 1394.0476 | 428.4 | 235.3818 | 7.5 | 1636.9294 | 316.7496 | 1320.1798 | 0 | 0 | 0 | 1047.6 | 0 | 0 | 0 | 272.5798 | 4 | 4 | 0 | 0 | 0 | 0 | 0
2 | 5 | 1260.7143 | 442.68 | 243.2279 | 7.5 | 1511.4421 | 310.7472 | 1200.6949 | 1 | 1 | 0 | 1017.045 | 1 | 1 | 0 | 228.6499 | 4 | 4 | 0 | 0 | 0 | 0 | 0
2 | 6 | 1282.1429 | 428.4 | 235.3818 | 7.5 | 1525.0247 | 268.9272 | 1256.0975 | 0 | 0 | 0 | 1047.6 | 0 | 0 | 0 | 208.4975 | 2 | 2 | 0 | 0 | 0 | 0 | 0
2 | 7 | 1309.5238 | 442.68 | 243.2279 | 7.5 | 1560.2517 | 238.8168 | 1321.4349 | 0 | 0 | 0 | 1082.52 | 1 | 1 | 0 | 238.9149 | 3 | 3 | 0 | 8.1148 | 36.8852 | 0 | 0
2 | 8 | 1258.3333 | 442.68 | 243.2279 | 7.5 | 1509.0612 | 253.5768 | 1255.4844 | 0 | 0 | 0 | 1082.52 | 0 | 0 | 0 | 172.9644 | 4 | 4 | 0 | 0 | 0 | 0 | 0
2 | 9 | 1352.381 | 428.4 | 235.3818 | 7.5 | 1595.2627 | 289.9848 | 1305.2779 | 0 | 0 | 0 | 1047.6 | 0 | 0 | 0 | 257.6779 | 5 | 5 | 0 | 0 | 0 | 0 | 0
2 | 10 | 1366.6667 | 442.68 | 243.2279 | 7.5 | 1617.3945 | 316.2576 | 1301.1369 | 1 | 1 | 0 | 1017.045 | 0 | 0 | 0 | 329.0919 | 4 | 4 | 0 | 0 | 0 | 0 | 0
2 | 11 | 1279.7619 | 178.5 | 0 | 7.5 | 1287.2619 | 284.2776 | 1002.9843 | 0 | 0 | 0 | 1002.9843 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0
2 | 12 | 1428.5714 | 184.45 | 0 | 7.5 | 1436.0714 | 282.8016 | 1153.2698 | 1 | 1 | 0 | 1017.045 | 1 | 1 | 0 | 181.2248 | 4 | 4 | 0 | 0 | 0 | 0 | 0
3 | 1 | 1391.6667 | 202.895 | 6.5272 | 7.5 | 1405.6938 | 296.0208 | 1109.673 | 1 | 1 | 0 | 1001.3175 | 0 | 0 | 0 | 153.3555 | 4 | 4 | 0 | 0 | 0 | 0 | 0
3 | 2 | 1410.7143 | 199.92 | 22.5555 | 6 | 1439.2698 | 288.896 | 1150.3738 | 0 | 0 | 0 | 962.64 | 1 | 1 | 0 | 187.7338 | 4 | 4 | 0 | 8.4444 | 36.5556 | 0 | 0
3 | 3 | 1259.5238 | 442.68 | 246.3122 | 7.5 | 1513.336 | 330.7664 | 1182.5696 | 1 | 1 | 0 | 1001.3175 | 1 | 1 | 0 | 226.2521 | 3 | 3 | 0 | 0 | 0 | 0 | 0
3 | 4 | 1394.0476 | 428.4 | 238.3666 | 7.5 | 1639.9142 | 314.1744 | 1325.7398 | 1 | 1 | 0 | 966.9375 | 1 | 1 | 0 | 403.8023 | 5 | 5 | 0 | 0 | 0 | 0 | 0
3 | 5 | 1260.7143 | 442.68 | 246.3122 | 7.5 | 1514.5265 | 308.2208 | 1206.3057 | 0 | 0 | 0 | 1065.78 | 1 | 1 | 0 | 140.5257 | 3 | 3 | 0 | 7.5312 | 37.4688 | 0 | 0
3 | 6 | 1282.1429 | 428.4 | 238.3666 | 7.5 | 1528.0095 | 266.7408 | 1261.2687 | 1 | 1 | 0 | 966.9375 | 1 | 1 | 0 | 339.3312 | 2 | 2 | 0 | 0 | 0 | 0 | 0
3 | 7 | 1309.5238 | 442.68 | 246.3122 | 7.5 | 1563.336 | 236.8752 | 1326.4608 | 1 | 1 | 0 | 1001.3175 | 1 | 1 | 0 | 370.1433 | 2 | 2 | 0 | 0 | 0 | 0 | 0
3 | 8 | 1258.3333 | 442.68 | 246.3122 | 7.5 | 1512.1455 | 251.5152 | 1260.6303 | 1 | 1 | 0 | 1001.3175 | 1 | 1 | 0 | 304.3128 | 4 | 4 | 0 | 0 | 0 | 0 | 0
3 | 9 | 1352.381 | 428.4 | 238.3666 | 7.5 | 1598.2476 | 287.6272 | 1310.6204 | 0 | 0 | 0 | 1031.4 | 1 | 1 | 0 | 279.2204 | 3 | 3 | 0 | 8.6217 | 36.3783 | 0 | 0
3 | 10 | 1366.6667 | 442.68 | 246.3122 | 7.5 | 1620.4788 | 313.6864 | 1306.7924 | 1 | 1 | 0 | 1001.3175 | 0 | 0 | 0 | 350.4749 | 3 | 3 | 0 | 0 | 0 | 0 | 0
3 | 11 | 1279.7619 | 178.5 | 0 | 7.5 | 1287.2619 | 281.9664 | 1005.2955 | 1 | 1 | 0 | 966.9375 | 1 | 1 | 0 | 83.358 | 3 | 3 | 0 | 0 | 0 | 0 | 0
3 | 12 | 1428.5714 | 184.45 | 0 | 7.5 | 1436.0714 | 280.5024 | 1155.569 | 1 | 1 | 0 | 1001.3175 | 1 | 1 | 0 | 199.2515 | 3 | 3 | 0 | 0 | 0 | 0 | 0
4 | 1 | 1391.6667 | 202.895 | 9.6115 | 7.5 | 1408.7781 | 293.5944 | 1115.1837 | 0 | 0 | 0 | 1049.04 | 1 | 1 | 0 | 66.1437 | 5 | 5 | 0 | 9.2005 | 35.7995 | 0 | 0
4 | 2 | 1410.7143 | 199.92 | 25.3413 | 6 | 1442.0556 | 286.528 | 1155.5276 | 1 | 1 | 0 | 884.07 | 1 | 1 | 0 | 316.4576 | 3 | 3 | 0 | 0 | 0 | 0 | 0
4 | 3 | 1259.5238 | 442.68 | 249.3965 | 7.5 | 1516.4203 | 328.0552 | 1188.3651 | 1 | 1 | 0 | 985.59 | 0 | 0 | 0 | 247.7751 | 3 | 3 | 0 | 0 | 0 | 0 | 0
4 | 4 | 1394.0476 | 428.4 | 241.3514 | 7.5 | 1642.899 | 311.5992 | 1331.2998 | 1 | 1 | 0 | 951.75 | 0 | 0 | 0 | 424.5498 | 2 | 2 | 0 | 0 | 0 | 0 | 0
4 | 5 | 1260.7143 | 442.68 | 249.3965 | 7.5 | 1517.6108 | 305.6944 | 1211.9164 | 1 | 1 | 0 | 985.59 | 0 | 0 | 0 | 271.3264 | 4 | 4 | 0 | 0 | 0 | 0 | 0
4 | 6 | 1282.1429 | 428.4 | 241.3514 | 7.5 | 1530.9943 | 264.5544 | 1266.4399 | 0 | 0 | 0 | 1015.2 | 1 | 1 | 0 | 251.2399 | 4 | 4 | 0 | 8.2953 | 36.7047 | 0 | 0
4 | 7 | 1309.5238 | 442.68 | 249.3965 | 7.5 | 1566.4203 | 234.9336 | 1331.4867 | 1 | 1 | 0 | 985.59 | 0 | 0 | 0 | 390.8967 | 3 | 3 | 0 | 0 | 0 | 0 | 0
4 | 8 | 1258.3333 | 442.68 | 249.3965 | 7.5 | 1515.2298 | 249.4536 | 1265.7762 | 0 | 0 | 0 | 1049.04 | 1 | 1 | 0 | 216.7362 | 4 | 4 | 0 | 8.1751 | 36.8249 | 0 | 0
4 | 9 | 1352.381 | 428.4 | 241.3514 | 7.5 | 1601.2324 | 285.2696 | 1315.9628 | 1 | 1 | 0 | 951.75 | 0 | 0 | 0 | 409.2128 | 3 | 3 | 0 | 0 | 0 | 0 | 0
4 | 10 | 1366.6667 | 442.68 | 249.3965 | 7.5 | 1623.5631 | 311.1152 | 1312.4479 | 0 | 0 | 0 | 1049.04 | 0 | 0 | 0 | 263.4079 | 2 | 2 | 0 | 0 | 0 | 0 | 0
4 | 11 | 1279.7619 | 178.5 | 0 | 7.5 | 1287.2619 | 279.6552 | 1007.6067 | 1 | 1 | 0 | 951.75 | 1 | 1 | 0 | 100.8567 | 4 | 4 | 0 | 0 | 0 | 0 | 0
4 | 12 | 1428.5714 | 184.45 | 0 | 7.5 | 1436.0714 | 278.2032 | 1157.8682 | 1 | 1 | 0 | 985.59 | 0 | 0 | 0 | 217.2782 | 4 | 4 | 0 | 0 | 0 | 0 | 0
5 | 1 | 1948.3333 | 202.895 | 12.6958 | 7.5 | 1968.5291 | 291.168 | 1677.3611 | 0 | 0 | 0 | 1032.3 | 0 | 0 | 0 | 645.0611 | 2 | 2 | 0 | 0 | 0 | 0 | 0
5 | 2 | 1975 | 199.92 | 28.1272 | 6 | 2009.1272 | 284.16 | 1724.9672 | 1 | 1 | 0 | 869.9625 | 1 | 1 | 0 | 918.0047 | 4 | 4 | 0 | 11.8221 | 51.1779 | 0 | 0
5 | 3 | 1763.3333 | 442.68 | 252.4808 | 7.5 | 2023.3141 | 325.344 | 1697.9701 | 1 | 1 | 0 | 969.8625 | 1 | 1 | 0 | 791.1076 | 3 | 3 | 0 | 10.9769 | 52.0231 | 0 | 0
5 | 4 | 1951.6667 | 428.4 | 244.3362 | 7.5 | 2203.5029 | 309.024 | 1894.4789 | 0 | 0 | 0 | 999 | 0 | 0 | 0 | 895.4789 | 3 | 3 | 0 | 0 | 0 | 0 | 0
5 | 5 | 1765 | 442.68 | 252.4808 | 7.5 | 2024.9808 | 303.168 | 1721.8128 | 0 | 0 | 0 | 1032.3 | 1 | 1 | 0 | 689.5128 | 4 | 4 | 0 | 10.5437 | 52.4563 | 0 | 0
5 | 6 | 1795 | 428.4 | 244.3362 | 7.5 | 2046.8362 | 262.368 | 1784.4682 | 0 | 0 | 0 | 999 | 0 | 0 | 0 | 785.4682 | 4 | 4 | 0 | 0 | 0 | 0 | 0
5 | 7 | 1833.3333 | 442.68 | 252.4808 | 7.5 | 2093.3141 | 232.992 | 1860.3221 | 1 | 1 | 0 | 969.8625 | 0 | 0 | 0 | 953.4596 | 3 | 3 | 0 | 0 | 0 | 0 | 0
5 | 8 | 1761.6667 | 442.68 | 252.4808 | 7.5 | 2021.6475 | 247.392 | 1774.2555 | 0 | 0 | 0 | 1032.3 | 1 | 1 | 0 | 741.9555 | 2 | 2 | 0 | 11.4452 | 51.5548 | 0 | 0
5 | 9 | 1893.3333 | 428.4 | 244.3362 | 7.5 | 2145.1696 | 282.912 | 1862.2576 | 0 | 0 | 0 | 999 | 1 | 1 | 0 | 863.2576 | 3 | 3 | 0 | 12.0703 | 50.9297 | 0 | 0
5 | 10 | 1913.3333 | 442.68 | 252.4808 | 7.5 | 2173.3141 | 308.544 | 1864.7701 | 1 | 1 | 0 | 969.8625 | 0 | 0 | 0 | 957.9076 | 4 | 4 | 0 | 0 | 0 | 0 | 0
5 | 11 | 1791.6667 | 178.5 | 0 | 7.5 | 1799.1667 | 277.344 | 1521.8227 | 0 | 0 | 0 | 999 | 1 | 1 | 0 | 522.8227 | 3 | 3 | 0 | 12.4787 | 50.5213 | 0 | 0
5 | 12 | 2000 | 184.45 | 0 | 7.5 | 2007.5 | 275.904 | 1731.596 | 1 | 1 | 0 | 969.8625 | 1 | 1 | 0 | 824.7335 | 4 | 4 | 0 | 12.3976 | 50.6024 | 0 | 0
6 | 1 | 1948.3333 | 202.895 | 15.7801 | 7.5 | 1971.6134 | 288.7416 | 1682.8718 | 1 | 1 | 0 | 954.135 | 0 | 0 | 0 | 791.7368 | 2 | 2 | 0 | 0 | 0 | 0 | 0
6 | 2 | 1975 | 199.92 | 30.913 | 6 | 2011.913 | 281.792 | 1730.121 | 1 | 1 | 0 | 855.855 | 1 | 1 | 0 | 937.266 | 4 | 4 | 0 | 11.8221 | 51.1779 | 0 | 0
6 | 3 | 1763.3333 | 442.68 | 255.5651 | 7.5 | 2026.3984 | 322.6328 | 1703.7656 | 0 | 0 | 0 | 1015.56 | 0 | 0 | 0 | 688.2056 | 4 | 4 | 0 | 0 | 0 | 0 | 0
6 | 4 | 1951.6667 | 428.4 | 247.3211 | 7.5 | 2206.4877 | 306.4488 | 1900.0389 | 0 | 0 | 0 | 982.8 | 1 | 1 | 0 | 917.2389 | 3 | 3 | 0 | 10.8477 | 52.1523 | 0 | 0
6 | 5 | 1765 | 442.68 | 255.5651 | 7.5 | 2028.0651 | 300.6416 | 1727.4235 | 1 | 1 | 0 | 954.135 | 0 | 0 | 0 | 836.2885 | 4 | 4 | 0 | 0 | 0 | 0 | 0
6 | 6 | 1795 | 428.4 | 247.3211 | 7.5 | 2049.8211 | 260.1816 | 1789.6395 | 0 | 0 | 0 | 982.8 | 0 | 0 | 0 | 806.8395 | 3 | 3 | 0 | 0 | 0 | 0 | 0
6 | 7 | 1833.3333 | 442.68 | 255.5651 | 7.5 | 2096.3984 | 231.0504 | 1865.348 | 1 | 1 | 0 | 954.135 | 0 | 0 | 0 | 974.213 | 3 | 3 | 0 | 0 | 0 | 0 | 0
6 | 8 | 1761.6667 | 442.68 | 255.5651 | 7.5 | 2024.7318 | 245.3304 | 1779.4014 | 1 | 1 | 0 | 954.135 | 1 | 1 | 0 | 888.2664 | 2 | 2 | 0 | 11.4452 | 51.5548 | 0 | 0
6 | 9 | 1893.3333 | 428.4 | 247.3211 | 7.5 | 2148.1544 | 280.5544 | 1867.6 | 1 | 1 | 0 | 921.375 | 0 | 0 | 0 | 1009.225 | 3 | 3 | 0 | 0 | 0 | 0 | 0
6 | 10 | 1913.3333 | 442.68 | 255.5651 | 7.5 | 2176.3984 | 305.9728 | 1870.4256 | 0 | 0 | 0 | 1015.56 | 0 | 0 | 0 | 854.8656 | 5 | 5 | 0 | 0 | 0 | 0 | 0
6 | 11 | 1791.6667 | 178.5 | 0 | 7.5 | 1799.1667 | 275.0328 | 1524.1339 | 0 | 0 | 0 | 982.8 | 0 | 0 | 0 | 541.3339 | 5 | 5 | 0 | 0 | 0 | 0 | 0
6 | 12 | 2000 | 184.45 | 0 | 7.5 | 2007.5 | 273.6048 | 1733.8952 | 0 | 0 | 0 | 1015.56 | 1 | 1 | 0 | 718.3352 | 3 | 3 | 0 | 12.3976 | 50.6024 | 0 | 0
7 | 1 | 1948.3333 | 202.895 | 18.8644 | 7.5 | 1974.6977 | 286.3152 | 1688.3825 | 1 | 1 | 0 | 938.4075 | 1 | 1 | 0 | 812.975 | 5 | 5 | 0 | 12.8807 | 50.1193 | 0 | 0
7 | 2 | 1975 | 199.92 | 33.6988 | 6 | 2014.6988 | 279.424 | 1735.2748 | 1 | 1 | 0 | 841.7475 | 0 | 0 | 0 | 956.5273 | 4 | 4 | 0 | 0 | 0 | 0 | 0
7 | 3 | 1763.3333 | 442.68 | 258.6494 | 7.5 | 2029.4827 | 319.9216 | 1709.5611 | 0 | 0 | 0 | 998.82 | 1 | 1 | 0 | 710.7411 | 2 | 2 | 0 | 10.9769 | 52.0231 | 0 | 0
7 | 4 | 1951.6667 | 428.4 | 250.3059 | 7.5 | 2209.4725 | 303.8736 | 1905.5989 | 0 | 0 | 0 | 966.6 | 0 | 0 | 0 | 938.9989 | 4 | 4 | 0 | 0 | 0 | 0 | 0
7 | 5 | 1765 | 442.68 | 258.6494 | 7.5 | 2031.1494 | 298.1152 | 1733.0342 | 0 | 0 | 0 | 998.82 | 1 | 1 | 0 | 734.2142 | 4 | 4 | 0 | 10.5437 | 52.4563 | 0 | 0
7 | 6 | 1795 | 428.4 | 250.3059 | 7.5 | 2052.8059 | 257.9952 | 1794.8107 | 0 | 0 | 0 | 966.6 | 0 | 0 | 0 | 828.2107 | 2 | 2 | 0 | 0 | 0 | 0 | 0
7 | 7 | 1833.3333 | 442.68 | 258.6494 | 7.5 | 2099.4827 | 229.1088 | 1870.3739 | 0 | 0 | 0 | 998.82 | 0 | 0 | 0 | 871.5539 | 2 | 2 | 0 | 0 | 0 | 0 | 0
7 | 8 | 1761.6667 | 442.68 | 258.6494 | 7.5 | 2027.8161 | 243.2688 | 1784.5473 | 0 | 0 | 0 | 998.82 | 0 | 0 | 0 | 785.7273 | 5 | 5 | 0 | 0 | 0 | 0 | 0
7 | 9 | 1893.3333 | 428.4 | 250.3059 | 7.5 | 2151.1392 | 278.1968 | 1872.9424 | 1 | 1 | 0 | 906.1875 | 1 | 1 | 0 | 1029.7549 | 4 | 4 | 0 | 12.0703 | 50.9297 | 0 | 0
7 | 10 | 1913.3333 | 442.68 | 258.6494 | 7.5 | 2179.4827 | 303.4016 | 1876.0811 | 1 | 1 | 0 | 938.4075 | 1 | 1 | 0 | 1000.6736 | 4 | 4 | 0 | 11.6971 | 51.3029 | 0 | 0
7 | 11 | 1791.6667 | 178.5 | 0.40588 | 7.5 | 1799.5725 | 272.7216 | 1526.8509 | 1 | 1 | 0 | 906.1875 | 1 | 1 | 0 | 683.6634 | 4 | 4 | 0 | 12.4787 | 50.5213 | 0 | 0
7 | 12 | 2000 | 184.45 | 0.41941 | 7.5 | 2007.9194 | 271.3056 | 1736.6138 | 0 | 0 | 0 | 998.82 | 0 | 0 | 0 | 737.7938 | 3 | 3 | 0 | 0 | 0 | 0 | 0
8 | 1 | 1948.3333 | 202.895 | 21.9487 | 7.5 | 1977.7821 | 283.8888 | 1693.8933 | 1 | 1 | 0 | 922.68 | 0 | 0 | 0 | 834.2133 | 5 | 5 | 0 | 0 | 0 | 0 | 0
8 | 2 | 1975 | 199.92 | 36.4847 | 6 | 2017.4847 | 277.056 | 1740.4287 | 1 | 1 | 0 | 827.64 | 1 | 1 | 0 | 975.7887 | 3 | 3 | 0 | 11.8221 | 51.1779 | 0 | 0
8 | 3 | 1763.3333 | 442.68 | 261.7337 | 7.5 | 2032.5671 | 317.2104 | 1715.3567 | 1 | 1 | 0 | 922.68 | 1 | 1 | 0 | 855.6767 | 5 | 5 | 0 | 10.9769 | 52.0231 | 0 | 0
8 | 4 | 1951.6667 | 428.4 | 253.2907 | 7.5 | 2212.4574 | 301.2984 | 1911.159 | 1 | 1 | 0 | 891 | 1 | 1 | 0 | 1083.159 | 5 | 5 | 0 | 10.8477 | 52.1523 | 0 | 0
8 | 5 | 1765 | 442.68 | 261.7337 | 7.5 | 2034.2337 | 295.5888 | 1738.6449 | 0 | 0 | 0 | 982.08 | 1 | 1 | 0 | 756.5649 | 5 | 5 | 0 | 10.5437 | 52.4563 | 0 | 0
8 | 6 | 1795 | 428.4 | 253.2907 | 7.5 | 2055.7907 | 255.8088 | 1799.9819 | 1 | 1 | 0 | 891 | 1 | 1 | 0 | 971.9819 | 3 | 3 | 0 | 11.6134 | 51.3866 | 0 | 0
8 | 7 | 1833.3333 | 442.68 | 261.7337 | 7.5 | 2102.5671 | 227.1672 | 1875.3999 | 1 | 1 | 0 | 922.68 | 1 | 1 | 0 | 1015.7199 | 3 | 3 | 0 | 11.3607 | 51.6393 | 0 | 0
8 | 8 | 1761.6667 | 442.68 | 261.7337 | 7.5 | 2030.9004 | 241.2072 | 1789.6932 | 1 | 1 | 0 | 922.68 | 1 | 1 | 0 | 930.0132 | 3 | 3 | 0 | 11.4452 | 51.5548 | 0 | 0
8 | 9 | 1893.3333 | 428.4 | 253.2907 | 7.5 | 2154.124 | 275.8392 | 1878.2848 | 1 | 1 | 0 | 891 | 1 | 1 | 0 | 1050.2848 | 3 | 3 | 0 | 12.0703 | 50.9297 | 0 | 0
8 | 10 | 1913.3333 | 442.68 | 261.7337 | 7.5 | 2182.5671 | 300.8304 | 1881.7367 | 0 | 0 | 0 | 982.08 | 1 | 1 | 0 | 899.6567 | 3 | 3 | 0 | 11.6971 | 51.3029 | 0 | 0
8 | 11 | 1791.6667 | 178.5 | 3.3907 | 7.5 | 1802.5574 | 270.4104 | 1532.147 | 1 | 1 | 0 | 891 | 1 | 1 | 0 | 704.147 | 3 | 3 | 0 | 12.4787 | 50.5213 | 0 | 0
8 | 12 | 2000 | 184.45 | 3.5037 | 7.5 | 2011.0037 | 269.0064 | 1741.9973 | 0 | 0 | 0 | 982.08 | 0 | 0 | 0 | 759.9173 | 4 | 4 | 0 | 0 | 0 | 0 | 0

## capex
year | Solar CAPEX, M PKR | BESS CAPEX, M PKR | Gas Generator CAPEX, M PKR | Existing Gas Generators CAPEX, M PKR | Grid CAPEX, M PKR | Diesel Generator CAPEX, M PKR
0 | 80 | 0 | 25 | 0 | 5 | 0
1 | 0 | 181 | 0 | 0 | 0 | 59
2 | 0 | 0 | 0 | 9 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 79
5 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0

## opex
year | month | Solar Depreciation Cost, M PKR | Solar Fixed Opex, M PKR | BESS Depreciation Cost, M PKR | BESS Fixed Opex, M PKR | Gas Generator Depreciation Cost, M PKR | Gas Generator Fixed Opex, M PKR | Gas Generator Var OPEX, M PKR | Fuel Charges for RLNG, M PKR | Existing Gas Generators Depreciation Cost, M PKR | Existing Gas Generators Fixed Opex, M PKR | Existing Gas Generators Var OPEX, M PKR | Fuel Charges for NG, M PKR | Grid Fixed Opex, M PKR | Grid Peak Rate Energy Cost, M PKR | Grid Offpeak Rate Energy Cost, M PKR | Diesel Generator Depreciation Cost, M PKR | Diesel Generator Fixed Opex, M PKR | Diesel Generator Var OPEX, M PKR | Fuel Charges for Diesel, M PKR | Loss due to Interruptions, M PKR | Loss due to Outage, M PKR
1 | 1 | 0.33333 | 0.385 | 1.5125 | 0.66 | 0.17361 | 0.495 | 4.2059 | 56.4798 | 0 | 0 | 0 | 0 | 2.277 | 1.2865 | 4.443 | 0.495 | 0.198 | 0 | 0 | 0 | 0
1 | 2 | 0.33333 | 0.385 | 1.5125 | 0.66 | 0.17361 | 0.495 | 3.8226 | 51.3319 | 0 | 0 | 0 | 0 | 2.277 | 1.5674 | 6.0224 | 0.495 | 0.198 | 0.024222 | 1.181 | 0 | 0
1 | 3 | 0.33333 | 0.385 | 1.5125 | 0.66 | 0.17361 | 0.495 | 4.2322 | 56.8317 | 0 | 0 | 0 | 0 | 2.277 | 1.1541 | 4.8547 | 0.495 | 0.198 | 0.030278 | 1.4763 | 0 | 0
1 | 4 | 0.33333 | 0.385 | 1.5125 | 0.66 | 0.17361 | 0.495 | 3.8679 | 51.9405 | 0 | 0 | 0 | 0 | 2.277 | 3.5402 | 15.1068 | 0.495 | 0.198 | 0 | 0 | 0 | 0
1 | 5 | 0.33333 | 0.385 | 1.5125 | 0.66 | 0.17361 | 0.495 | 4.2322 | 56.8317 | 0 | 0 | 0 | 0 | 2.277 | 0.91009 | 4.0188 | 0.495 | 0.198 | 0.030278 | 1.4763 | 0 | 0
1 | 6 | 0.33333 | 0.385 | 1.5125 | 0.66 | 0.17361 | 0.495 | 3.8679 | 51.9405 | 0 | 0 | 0 | 0 | 2.277 | 3.1238 | 12.2683 | 0.495 | 0.198 | 0 | 0 | 0 | 0
1 | 7 | 0.33333 | 0.385 | 1.5125 | 0.66 | 0.17361 | 0.495 | 4.2322 | 56.8317 | 0 | 0 | 0 | 0 | 2.277 | 2.6827 | 10.8231 | 0.495 | 0.198 | 0.018166 | 0.88577 | 0 | 0
1 | 8 | 0.33333 | 0.385 | 1.5125 | 0.66 | 0.17361 | 0.495 | 4.2322 | 56.8317 | 0 | 0 | 0 | 0 | 2.277 | 1.5576 | 6.2272 | 0.495 | 0.198 | 0.024222 | 1.181 | 0 | 0
1 | 9 | 0.33333 | 0.385 | 1.5125 | 0.66 | 0.17361 | 0.495 | 4.0694 | 54.6465 | 0 | 0 | 0 | 0 | 2.277 | 3.7796 | 14.1547 | 0.495 | 0.198 | 0 | 0 | 0 | 0
1 | 10 | 0.33333 | 0.385 | 1.5125 | 0.66 | 0.17361 | 0.495 | 4.2322 | 56.8317 | 0 | 0 | 0 | 0 | 2.277 | 2.5416 | 9.8942 | 0.495 | 0.198 | 0.030278 | 1.4763 | 0 | 0
1 | 11 | 0.33333 | 0.385 | 1.5125 | 0.66 | 0.17361 | 0.495 | 4.0541 | 54.4408 | 0 | 0 | 0 | 0 | 2.277 | 0 | 0 | 0.495 | 0.198 | 0 | 0 | 0 | 0
1 | 12 | 0.33333 | 0.385 | 1.5125 | 0.66 | 0.17361 | 0.495 | 4.0468 | 54.343 | 0 | 0 | 0 | 0 | 2.277 | 1.8225 | 6.6025 | 0.495 | 0.198 | 0 | 0 | 0 | 0
2 | 1 | 0.33333 | 0.4235 | 1.5125 | 0.726 | 0.17361 | 0.5445 | 4.3383 | 58.2568 | 0.20833 | 0.726 | 0.55952 | 6.6383 | 2.5047 | 0 | 0 | 0.495 | 0.2178 | 0 | 0 | 0 | 0
2 | 2 | 0.33333 | 0.4235 | 1.5125 | 0.726 | 0.17361 | 0.5445 | 3.9102 | 52.5078 | 0.20833 | 0.726 | 1.1771 | 13.9649 | 2.5047 | 0 | 0 | 0.495 | 0.2178 | 0 | 0 | 0 | 0
2 | 3 | 0.33333 | 0.4235 | 1.5125 | 0.726 | 0.17361 | 0.5445 | 4.3538 | 58.4655 | 0.20833 | 0.726 | 0.86703 | 10.2867 | 2.5047 | 0 | 0 | 0.495 | 0.2178 | 0 | 0 | 0 | 0
2 | 4 | 0.33333 | 0.4235 | 1.5125 | 0.726 | 0.17361 | 0.5445 | 4.4366 | 59.577 | 0.20833 | 0.726 | 1.2165 | 14.4334 | 2.5047 | 0 | 0 | 0.495 | 0.2178 | 0 | 0 | 0 | 0
2 | 5 | 0.33333 | 0.4235 | 1.5125 | 0.726 | 0.17361 | 0.5445 | 4.5599 | 61.2334 | 0.20833 | 0.726 | 0.96833 | 11.4886 | 2.5047 | 0 | 0 | 0.495 | 0.2178 | 0 | 0 | 0 | 0
2 | 6 | 0.33333 | 0.4235 | 1.5125 | 0.726 | 0.17361 | 0.5445 | 4.4366 | 59.577 | 0.20833 | 0.726 | 0.91407 | 10.8448 | 2.5047 | 0 | 0 | 0.495 | 0.2178 | 0 | 0 | 0 | 0
2 | 7 | 0.33333 | 0.4235 | 1.5125 | 0.726 | 0.17361 | 0.5445 | 4.5845 | 61.5629 | 0.20833 | 0.726 | 1.0584 | 12.5575 | 2.5047 | 0.50655 | 2.0437 | 0.495 | 0.2178 | 0 | 0 | 0 | 0
2 | 8 | 0.33333 | 0.4235 | 1.5125 | 0.726 | 0.17361 | 0.5445 | 4.5845 | 61.5629 | 0.20833 | 0.726 | 0.79467 | 9.4282 | 2.5047 | 0 | 0 | 0.495 | 0.2178 | 0 | 0 | 0 | 0
2 | 9 | 0.33333 | 0.4235 | 1.5125 | 0.726 | 0.17361 | 0.5445 | 4.4366 | 59.577 | 0.20833 | 0.726 | 1.169 | 13.8691 | 2.5047 | 0 | 0 | 0.495 | 0.2178 | 0 | 0 | 0 | 0
2 | 10 | 0.33333 | 0.4235 | 1.5125 | 0.726 | 0.17361 | 0.5445 | 4.3694 | 58.6742 | 0.20833 | 0.726 | 1.3937 | 16.5353 | 2.5047 | 0 | 0 | 0.495 | 0.2178 | 0 | 0 | 0 | 0
2 | 11 | 0.33333 | 0.4235 | 1.5125 | 0.726 | 0.17361 | 0.5445 | 4.2787 | 57.4571 | 0.20833 | 0.726 | 0 | 0 | 2.5047 | 0 | 0 | 0.495 | 0.2178 | 0 | 0 | 0 | 0
2 | 12 | 0.33333 | 0.4235 | 1.5125 | 0.726 | 0.17361 | 0.5445 | 4.5599 | 61.2334 | 0.20833 | 0.726 | 0.76749 | 9.1057 | 2.5047 | 0 | 0 | 0.495 | 0.2178 | 0 | 0 | 0 | 0
3 | 1 | 0.33333 | 0.46585 | 1.5125 | 0.7986 | 0.17361 | 0.59895 | 4.733 | 63.5578 | 0.20833 | 0.7986 | 0.71441 | 8.4759 | 2.7552 | 0 | 0 | 0.495 | 0.23958 | 0 | 0 | 0 | 0
3 | 2 | 0.33333 | 0.46585 | 1.5125 | 0.7986 | 0.17361 | 0.59895 | 4.4845 | 60.2199 | 0.20833 | 0.7986 | 0.94294 | 11.1874 | 2.7552 | 0.57984 | 2.2279 | 0.495 | 0.23958 | 0 | 0 | 0 | 0
3 | 3 | 0.33333 | 0.46585 | 1.5125 | 0.7986 | 0.17361 | 0.59895 | 4.9256 | 66.1432 | 0.20833 | 0.7986 | 1.054 | 12.5049 | 2.7552 | 0 | 0 | 0.495 | 0.23958 | 0 | 0 | 0 | 0
3 | 4 | 0.33333 | 0.46585 | 1.5125 | 0.7986 | 0.17361 | 0.59895 | 4.7996 | 64.4517 | 0.20833 | 0.7986 | 1.8811 | 22.3181 | 2.7552 | 0 | 0 | 0.495 | 0.23958 | 0 | 0 | 0 | 0
3 | 5 | 0.33333 | 0.46585 | 1.5125 | 0.7986 | 0.17361 | 0.59895 | 4.9649 | 66.672 | 0.20833 | 0.7986 | 0.70593 | 8.3753 | 2.7552 | 0.51714 | 2.2836 | 0.495 | 0.23958 | 0 | 0 | 0 | 0
3 | 6 | 0.33333 | 0.46585 | 1.5125 | 0.7986 | 0.17361 | 0.59895 | 4.7483 | 63.7629 | 0.20833 | 0.7986 | 1.5808 | 18.7548 | 2.7552 | 0 | 0 | 0.495 | 0.23958 | 0 | 0 | 0 | 0
3 | 7 | 0.33333 | 0.46585 | 1.5125 | 0.7986 | 0.17361 | 0.59895 | 4.9085 | 65.9137 | 0.20833 | 0.7986 | 1.7243 | 20.4577 | 2.7552 | 0 | 0 | 0.495 | 0.23958 | 0 | 0 | 0 | 0
3 | 8 | 0.33333 | 0.46585 | 1.5125 | 0.7986 | 0.17361 | 0.59895 | 4.9427 | 66.3728 | 0.20833 | 0.7986 | 1.4176 | 16.8193 | 2.7552 | 0 | 0 | 0.495 | 0.23958 | 0 | 0 | 0 | 0
3 | 9 | 0.33333 | 0.46585 | 1.5125 | 0.7986 | 0.17361 | 0.59895 | 4.8048 | 64.5213 | 0.20833 | 0.7986 | 1.352 | 16.041 | 2.7552 | 0.59202 | 2.2171 | 0.495 | 0.23958 | 0 | 0 | 0 | 0
3 | 10 | 0.33333 | 0.46585 | 1.5125 | 0.7986 | 0.17361 | 0.59895 | 4.7159 | 63.3282 | 0.20833 | 0.7986 | 1.6327 | 19.3707 | 2.7552 | 0 | 0 | 0.495 | 0.23958 | 0 | 0 | 0 | 0
3 | 11 | 0.33333 | 0.46585 | 1.5125 | 0.7986 | 0.17361 | 0.59895 | 4.7654 | 63.9925 | 0.20833 | 0.7986 | 0.38832 | 4.6072 | 2.7552 | 0 | 0 | 0.495 | 0.23958 | 0 | 0 | 0 | 0
3 | 12 | 0.33333 | 0.46585 | 1.5125 | 0.7986 | 0.17361 | 0.59895 | 4.9256 | 66.1432 | 0.20833 | 0.7986 | 0.92821 | 11.0126 | 2.7552 | 0 | 0 | 0.495 | 0.23958 | 0 | 0 | 0 | 0
4 | 1 | 0.33333 | 0.51244 | 1.5125 | 0.87846 | 0.17361 | 0.65885 | 5.3756 | 72.1873 | 0.20833 | 0.87846 | 0.43298 | 5.1369 | 3.0307 | 0.69494 | 2.4 | 1.1538 | 0.52708 | 0 | 0 | 0 | 0
4 | 2 | 0.33333 | 0.51244 | 1.5125 | 0.87846 | 0.17361 | 0.65885 | 4.8173 | 64.6894 | 0.20833 | 0.87846 | 1.6216 | 19.2396 | 3.0307 | 0 | 0 | 1.1538 | 0.52708 | 0 | 0 | 0 | 0
4 | 3 | 0.33333 | 0.51244 | 1.5125 | 0.87846 | 0.17361 | 0.65885 | 5.1069 | 68.5787 | 0.20833 | 0.87846 | 1.2697 | 15.0639 | 3.0307 | 0 | 0 | 1.1538 | 0.52708 | 0 | 0 | 0 | 0
4 | 4 | 0.33333 | 0.51244 | 1.5125 | 0.87846 | 0.17361 | 0.65885 | 4.9147 | 65.9976 | 0.20833 | 0.87846 | 2.1755 | 25.8113 | 3.0307 | 0 | 0 | 1.1538 | 0.52708 | 0 | 0 | 0 | 0
4 | 5 | 0.33333 | 0.51244 | 1.5125 | 0.87846 | 0.17361 | 0.65885 | 5.1257 | 68.8313 | 0.20833 | 0.87846 | 1.3904 | 16.4958 | 3.0307 | 0 | 0 | 1.1538 | 0.52708 | 0 | 0 | 0 | 0
4 | 6 | 0.33333 | 0.51244 | 1.5125 | 0.87846 | 0.17361 | 0.65885 | 5.2022 | 69.8587 | 0.20833 | 0.87846 | 1.3627 | 16.1671 | 3.0307 | 0.62657 | 2.4607 | 1.1538 | 0.52708 | 0 | 0 | 0 | 0
4 | 7 | 0.33333 | 0.51244 | 1.5125 | 0.87846 | 0.17361 | 0.65885 | 5.1069 | 68.5787 | 0.20833 | 0.87846 | 2.0031 | 23.7652 | 3.0307 | 0 | 0 | 1.1538 | 0.52708 | 0 | 0 | 0 | 0
4 | 8 | 0.33333 | 0.51244 | 1.5125 | 0.87846 | 0.17361 | 0.65885 | 5.3756 | 72.1873 | 0.20833 | 0.87846 | 1.1859 | 14.0694 | 3.0307 | 0.61749 | 2.4688 | 1.1538 | 0.52708 | 0 | 0 | 0 | 0
4 | 9 | 0.33333 | 0.51244 | 1.5125 | 0.87846 | 0.17361 | 0.65885 | 4.9335 | 66.2501 | 0.20833 | 0.87846 | 2.0969 | 24.8788 | 3.0307 | 0 | 0 | 1.1538 | 0.52708 | 0 | 0 | 0 | 0
4 | 10 | 0.33333 | 0.51244 | 1.5125 | 0.87846 | 0.17361 | 0.65885 | 5.3756 | 72.1873 | 0.20833 | 0.87846 | 1.3874 | 16.4606 | 3.0307 | 0 | 0 | 1.1538 | 0.52708 | 0 | 0 | 0 | 0
4 | 11 | 0.33333 | 0.51244 | 1.5125 | 0.87846 | 0.17361 | 0.65885 | 5.1829 | 69.5992 | 0.20833 | 0.87846 | 0.51683 | 6.1318 | 3.0307 | 0 | 0 | 1.1538 | 0.52708 | 0 | 0 | 0 | 0
4 | 12 | 0.33333 | 0.51244 | 1.5125 | 0.87846 | 0.17361 | 0.65885 | 5.1257 | 68.8313 | 0.20833 | 0.87846 | 1.1134 | 13.2098 | 3.0307 | 0 | 0 | 1.1538 | 0.52708 | 0 | 0 | 0 | 0
5 | 1 | 0.33333 | 0.56368 | 1.5125 | 0.96631 | 0.17361 | 0.72473 | 5.8189 | 78.1389 | 0.20833 | 0.96631 | 3.694 | 43.8266 | 3.3338 | 0 | 0 | 1.1538 | 0.57978 | 0 | 0 | 0 | 0
5 | 2 | 0.33333 | 0.56368 | 1.5125 | 0.96631 | 0.17361 | 0.72473 | 4.9038 | 65.8509 | 0.20833 | 0.96631 | 5.2904 | 62.7673 | 3.3338 | 0.98225 | 3.7741 | 1.1538 | 0.57978 | 0 | 0 | 0 | 0
5 | 3 | 0.33333 | 0.56368 | 1.5125 | 0.96631 | 0.17361 | 0.72473 | 5.4669 | 73.4127 | 0.20833 | 0.96631 | 4.5462 | 53.9373 | 3.3338 | 0.91203 | 3.8365 | 1.1538 | 0.57978 | 0 | 0 | 0 | 0
5 | 4 | 0.33333 | 0.56368 | 1.5125 | 0.96631 | 0.17361 | 0.72473 | 5.6311 | 75.6183 | 0.20833 | 0.96631 | 5.1345 | 60.9173 | 3.3338 | 0 | 0 | 1.1538 | 0.57978 | 0 | 0 | 0 | 0
5 | 5 | 0.33333 | 0.56368 | 1.5125 | 0.96631 | 0.17361 | 0.72473 | 5.8189 | 78.1389 | 0.20833 | 0.96631 | 4.0025 | 47.4866 | 3.3338 | 0.87604 | 3.8684 | 1.1538 | 0.57978 | 0 | 0 | 0 | 0
5 | 6 | 0.33333 | 0.56368 | 1.5125 | 0.96631 | 0.17361 | 0.72473 | 5.6311 | 75.6183 | 0.20833 | 0.96631 | 4.5434 | 53.9038 | 3.3338 | 0 | 0 | 1.1538 | 0.57978 | 0 | 0 | 0 | 0
5 | 7 | 0.33333 | 0.56368 | 1.5125 | 0.96631 | 0.17361 | 0.72473 | 5.4669 | 73.4127 | 0.20833 | 0.96631 | 5.4613 | 64.7948 | 3.3338 | 0 | 0 | 1.1538 | 0.57978 | 0 | 0 | 0 | 0
5 | 8 | 0.33333 | 0.56368 | 1.5125 | 0.96631 | 0.17361 | 0.72473 | 5.8189 | 78.1389 | 0.20833 | 0.96631 | 4.2402 | 50.3066 | 3.3338 | 0.95094 | 3.8019 | 1.1538 | 0.57978 | 0 | 0 | 0 | 0
5 | 9 | 0.33333 | 0.56368 | 1.5125 | 0.96631 | 0.17361 | 0.72473 | 5.6311 | 75.6183 | 0.20833 | 0.96631 | 4.9529 | 58.7624 | 3.3338 | 1.0029 | 3.7558 | 1.1538 | 0.57978 | 0 | 0 | 0 | 0
5 | 10 | 0.33333 | 0.56368 | 1.5125 | 0.96631 | 0.17361 | 0.72473 | 5.4669 | 73.4127 | 0.20833 | 0.96631 | 5.5154 | 65.4359 | 3.3338 | 0 | 0 | 1.1538 | 0.57978 | 0 | 0 | 0 | 0
5 | 11 | 0.33333 | 0.56368 | 1.5125 | 0.96631 | 0.17361 | 0.72473 | 5.6311 | 75.6183 | 0.20833 | 0.96631 | 3.0339 | 35.9953 | 3.3338 | 1.0368 | 3.7257 | 1.1538 | 0.57978 | 0 | 0 | 0 | 0
5 | 12 | 0.33333 | 0.56368 | 1.5125 | 0.96631 | 0.17361 | 0.72473 | 5.4669 | 73.4127 | 0.20833 | 0.96631 | 4.7647 | 56.5297 | 3.3338 | 1.0301 | 3.7317 | 1.1538 | 0.57978 | 0 | 0 | 0 | 0
6 | 1 | 0.33333 | 0.62005 | 1.5125 | 1.0629 | 0.17361 | 0.7972 | 5.9161 | 79.4445 | 0.20833 | 1.0629 | 4.9729 | 58.9993 | 3.6671 | 0 | 0 | 1.1538 | 0.63776 | 0 | 0 | 0 | 0
6 | 2 | 0.33333 | 0.62005 | 1.5125 | 1.0629 | 0.17361 | 0.7972 | 5.3067 | 71.2614 | 0.20833 | 1.0629 | 5.9389 | 70.461 | 3.6671 | 1.0805 | 4.1515 | 1.1538 | 0.63776 | 0 | 0 | 0 | 0
6 | 3 | 0.33333 | 0.62005 | 1.5125 | 1.0629 | 0.17361 | 0.7972 | 6.2969 | 84.5589 | 0.20833 | 1.0629 | 4.3946 | 52.1391 | 3.6671 | 0 | 0 | 1.1538 | 0.63776 | 0 | 0 | 0 | 0
6 | 4 | 0.33333 | 0.62005 | 1.5125 | 1.0629 | 0.17361 | 0.7972 | 6.0938 | 81.8312 | 0.20833 | 1.0629 | 5.7829 | 68.6097 | 3.6671 | 0.99142 | 4.2306 | 1.1538 | 0.63776 | 0 | 0 | 0 | 0
6 | 5 | 0.33333 | 0.62005 | 1.5125 | 1.0629 | 0.17361 | 0.7972 | 5.9161 | 79.4445 | 0.20833 | 1.0629 | 5.3128 | 63.0327 | 3.6671 | 0 | 0 | 1.1538 | 0.63776 | 0 | 0 | 0 | 0
6 | 6 | 0.33333 | 0.62005 | 1.5125 | 1.0629 | 0.17361 | 0.7972 | 6.0938 | 81.8312 | 0.20833 | 1.0629 | 5.0984 | 60.4883 | 3.6671 | 0 | 0 | 1.1538 | 0.63776 | 0 | 0 | 0 | 0
6 | 7 | 0.33333 | 0.62005 | 1.5125 | 1.0629 | 0.17361 | 0.7972 | 5.9161 | 79.4445 | 0.20833 | 1.0629 | 6.1361 | 72.801 | 3.6671 | 0 | 0 | 1.1538 | 0.63776 | 0 | 0 | 0 | 0
6 | 8 | 0.33333 | 0.62005 | 1.5125 | 1.0629 | 0.17361 | 0.7972 | 5.9161 | 79.4445 | 0.20833 | 1.0629 | 5.5714 | 66.1004 | 3.6671 | 1.046 | 4.1821 | 1.1538 | 0.63776 | 0 | 0 | 0 | 0
6 | 9 | 0.33333 | 0.62005 | 1.5125 | 1.0629 | 0.17361 | 0.7972 | 5.713 | 76.7168 | 0.20833 | 1.0629 | 6.3532 | 75.3766 | 3.6671 | 0 | 0 | 1.1538 | 0.63776 | 0 | 0 | 0 | 0
6 | 10 | 0.33333 | 0.62005 | 1.5125 | 1.0629 | 0.17361 | 0.7972 | 6.2969 | 84.5589 | 0.20833 | 1.0629 | 5.4599 | 64.7773 | 3.6671 | 0 | 0 | 1.1538 | 0.63776 | 0 | 0 | 0 | 0
6 | 11 | 0.33333 | 0.62005 | 1.5125 | 1.0629 | 0.17361 | 0.7972 | 6.0938 | 81.8312 | 0.20833 | 1.0629 | 3.5158 | 41.7126 | 3.6671 | 0 | 0 | 1.1538 | 0.63776 | 0 | 0 | 0 | 0
6 | 12 | 0.33333 | 0.62005 | 1.5125 | 1.0629 | 0.17361 | 0.7972 | 6.2969 | 84.5589 | 0.20833 | 1.0629 | 4.5496 | 53.9776 | 3.6671 | 1.1331 | 4.1049 | 1.1538 | 0.63776 | 0 | 0 | 0 | 0
7 | 1 | 0.33333 | 0.68205 | 1.5125 | 1.1692 | 0.17361 | 0.87692 | 6.4004 | 85.9485 | 0.20833 | 1.1692 | 5.7201 | 67.8652 | 4.0338 | 1.2949 | 4.4722 | 1.1538 | 0.70154 | 0 | 0 | 0 | 0
7 | 2 | 0.33333 | 0.68205 | 1.5125 | 1.1692 | 0.17361 | 0.87692 | 5.7411 | 77.0954 | 0.20833 | 1.1692 | 6.6642 | 79.0657 | 4.0338 | 0 | 0 | 1.1538 | 0.70154 | 0 | 0 | 0 | 0
7 | 3 | 0.33333 | 0.68205 | 1.5125 | 1.1692 | 0.17361 | 0.87692 | 6.8125 | 91.4816 | 0.20833 | 1.1692 | 4.9177 | 58.3451 | 4.0338 | 1.1036 | 4.6421 | 1.1538 | 0.70154 | 0 | 0 | 0 | 0
7 | 4 | 0.33333 | 0.68205 | 1.5125 | 1.1692 | 0.17361 | 0.87692 | 6.5927 | 88.5306 | 0.20833 | 1.1692 | 6.5446 | 77.6473 | 4.0338 | 0 | 0 | 1.1538 | 0.70154 | 0 | 0 | 0 | 0
7 | 5 | 0.33333 | 0.68205 | 1.5125 | 1.1692 | 0.17361 | 0.87692 | 6.8125 | 91.4816 | 0.20833 | 1.1692 | 5.1479 | 61.076 | 4.0338 | 1.06 | 4.6808 | 1.1538 | 0.70154 | 0 | 0 | 0 | 0
7 | 6 | 0.33333 | 0.68205 | 1.5125 | 1.1692 | 0.17361 | 0.87692 | 6.5927 | 88.5306 | 0.20833 | 1.1692 | 5.7189 | 67.8507 | 4.0338 | 0 | 0 | 1.1538 | 0.70154 | 0 | 0 | 0 | 0
7 | 7 | 0.33333 | 0.68205 | 1.5125 | 1.1692 | 0.17361 | 0.87692 | 6.8125 | 91.4816 | 0.20833 | 1.1692 | 6.0145 | 71.3581 | 4.0338 | 0 | 0 | 1.1538 | 0.70154 | 0 | 0 | 0 | 0
7 | 8 | 0.33333 | 0.68205 | 1.5125 | 1.1692 | 0.17361 | 0.87692 | 6.8125 | 91.4816 | 0.20833 | 1.1692 | 5.5343 | 65.6603 | 4.0338 | 0 | 0 | 1.1538 | 0.70154 | 0 | 0 | 0 | 0
7 | 9 | 0.33333 | 0.68205 | 1.5125 | 1.1692 | 0.17361 | 0.87692 | 6.1807 | 82.9974 | 0.20833 | 1.1692 | 7.1636 | 84.9913 | 4.0338 | 1.2135 | 4.5445 | 1.1538 | 0.70154 | 0 | 0 | 0 | 0
7 | 10 | 0.33333 | 0.68205 | 1.5125 | 1.1692 | 0.17361 | 0.87692 | 6.4004 | 85.9485 | 0.20833 | 1.1692 | 6.9653 | 82.6381 | 4.0338 | 1.176 | 4.5779 | 1.1538 | 0.70154 | 0 | 0 | 0 | 0
7 | 11 | 0.33333 | 0.68205 | 1.5125 | 1.1692 | 0.17361 | 0.87692 | 6.1807 | 82.9974 | 0.20833 | 1.1692 | 4.8031 | 56.9855 | 4.0338 | 1.2545 | 4.5081 | 1.1538 | 0.70154 | 0 | 0 | 0 | 0
7 | 12 | 0.33333 | 0.68205 | 1.5125 | 1.1692 | 0.17361 | 0.87692 | 6.8125 | 91.4816 | 0.20833 | 1.1692 | 5.1373 | 60.9499 | 4.0338 | 0 | 0 | 1.1538 | 0.70154 | 0 | 0 | 0 | 0
8 | 1 | 0.33333 | 0.75026 | 1.5125 | 1.2862 | 0.17361 | 0.96461 | 6.9225 | 92.9588 | 0.20833 | 1.2862 | 6.4515 | 76.5422 | 4.4372 | 0 | 0 | 1.1538 | 0.77169 | 0 | 0 | 0 | 0
8 | 2 | 0.33333 | 0.75026 | 1.5125 | 1.2862 | 0.17361 | 0.96461 | 6.2094 | 83.3836 | 0.20833 | 1.2862 | 7.4366 | 88.2295 | 4.4372 | 1.3074 | 5.0234 | 1.1538 | 0.77169 | 0 | 0 | 0 | 0
8 | 3 | 0.33333 | 0.75026 | 1.5125 | 1.2862 | 0.17361 | 0.96461 | 6.9225 | 92.9588 | 0.20833 | 1.2862 | 6.6125 | 78.4527 | 4.4372 | 1.2139 | 5.1063 | 1.1538 | 0.77169 | 0 | 0 | 0 | 0
8 | 4 | 0.33333 | 0.75026 | 1.5125 | 1.2862 | 0.17361 | 0.96461 | 6.6848 | 89.7671 | 0.20833 | 1.2862 | 8.3192 | 98.7014 | 4.4372 | 1.1996 | 5.119 | 1.1538 | 0.77169 | 0 | 0 | 0 | 0
8 | 5 | 0.33333 | 0.75026 | 1.5125 | 1.2862 | 0.17361 | 0.96461 | 7.3681 | 98.9433 | 0.20833 | 1.2862 | 5.8689 | 69.6305 | 4.4372 | 1.166 | 5.1488 | 1.1538 | 0.77169 | 0 | 0 | 0 | 0
8 | 6 | 0.33333 | 0.75026 | 1.5125 | 1.2862 | 0.17361 | 0.96461 | 6.6848 | 89.7671 | 0.20833 | 1.2862 | 7.408 | 87.8906 | 4.4372 | 1.2843 | 5.0439 | 1.1538 | 0.77169 | 0 | 0 | 0 | 0
8 | 7 | 0.33333 | 0.75026 | 1.5125 | 1.2862 | 0.17361 | 0.96461 | 6.9225 | 92.9588 | 0.20833 | 1.2862 | 7.7361 | 91.7838 | 4.4372 | 1.2563 | 5.0687 | 1.1538 | 0.77169 | 0 | 0 | 0 | 0
8 | 8 | 0.33333 | 0.75026 | 1.5125 | 1.2862 | 0.17361 | 0.96461 | 6.9225 | 92.9588 | 0.20833 | 1.2862 | 7.0931 | 84.1549 | 4.4372 | 1.2657 | 5.0604 | 1.1538 | 0.77169 | 0 | 0 | 0 | 0
8 | 9 | 0.33333 | 0.75026 | 1.5125 | 1.2862 | 0.17361 | 0.96461 | 6.6848 | 89.7671 | 0.20833 | 1.2862 | 7.9955 | 94.8605 | 4.4372 | 1.3348 | 4.999 | 1.1538 | 0.77169 | 0 | 0 | 0 | 0
8 | 10 | 0.33333 | 0.75026 | 1.5125 | 1.2862 | 0.17361 | 0.96461 | 7.3681 | 98.9433 | 0.20833 | 1.2862 | 6.8654 | 81.4528 | 4.4372 | 1.2936 | 5.0356 | 1.1538 | 0.77169 | 0 | 0 | 0 | 0
8 | 11 | 0.33333 | 0.75026 | 1.5125 | 1.2862 | 0.17361 | 0.96461 | 6.6848 | 89.7671 | 0.20833 | 1.2862 | 5.3985 | 64.0499 | 4.4372 | 1.38 | 4.9589 | 1.1538 | 0.77169 | 0 | 0 | 0 | 0
8 | 12 | 0.33333 | 0.75026 | 1.5125 | 1.2862 | 0.17361 | 0.96461 | 7.3681 | 98.9433 | 0.20833 | 1.2862 | 5.8555 | 69.4715 | 4.4372 | 0 | 0 | 1.1538 | 0.77169 | 0 | 0 | 0 | 0

## emissions
year | month | CO2 Emissions from Gas Generator, MT | CO2 Emissions from Existing Gas Generators, MT | CO2 Emissions from Grid, MT | CO2 Emissions from Diesel Generator, MT
1 | 1 | 218.4905 | 0 | 19.9582 | 0
1 | 2 | 198.576 | 0 | 26.4935 | 7.34
1 | 3 | 219.852 | 0 | 21.0093 | 9.175
1 | 4 | 200.9305 | 0 | 65.2153 | 0
1 | 5 | 219.852 | 0 | 17.2484 | 9.175
1 | 6 | 200.9305 | 0 | 53.7505 | 0
1 | 7 | 219.852 | 0 | 47.1868 | 5.505
1 | 8 | 219.852 | 0 | 27.1941 | 7.34
1 | 9 | 211.3985 | 0 | 62.5721 | 0
1 | 10 | 219.852 | 0 | 43.4199 | 9.175
1 | 11 | 210.6026 | 0 | 0 | 0
1 | 12 | 210.2245 | 0 | 29.3757 | 0
2 | 1 | 204.877 | 26.4235 | 0 | 0
2 | 2 | 184.659 | 55.587 | 0 | 0
2 | 3 | 205.611 | 40.9458 | 0 | 0
2 | 4 | 209.52 | 57.452 | 0 | 0
2 | 5 | 215.345 | 45.73 | 0 | 0
2 | 6 | 209.52 | 43.1675 | 0 | 0
2 | 7 | 216.504 | 49.985 | 8.1 | 0
2 | 8 | 216.504 | 37.5289 | 0 | 0
2 | 9 | 209.52 | 55.2056 | 0 | 0
2 | 10 | 206.345 | 65.8184 | 0 | 0
2 | 11 | 202.0649 | 0 | 0 | 0
2 | 12 | 215.345 | 36.245 | 0 | 0
3 | 1 | 203.1995 | 30.6711 | 0 | 0
3 | 2 | 192.528 | 40.4828 | 8.1 | 0
3 | 3 | 211.4655 | 45.2504 | 0 | 0
3 | 4 | 206.0575 | 80.7605 | 0 | 0
3 | 5 | 213.156 | 30.3071 | 8.1 | 0
3 | 6 | 203.8555 | 67.8662 | 0 | 0
3 | 7 | 210.7315 | 74.0287 | 0 | 0
3 | 8 | 212.1995 | 60.8626 | 0 | 0
3 | 9 | 206.28 | 58.0461 | 8.1 | 0
3 | 10 | 202.4655 | 70.095 | 0 | 0
3 | 11 | 204.5895 | 16.6716 | 0 | 0
3 | 12 | 211.4655 | 39.8503 | 0 | 0
4 | 1 | 209.808 | 16.8987 | 8.1 | 0
4 | 2 | 188.016 | 63.2915 | 0 | 0
4 | 3 | 199.32 | 49.555 | 0 | 0
4 | 4 | 191.818 | 84.91 | 0 | 0
4 | 5 | 200.054 | 54.2653 | 0 | 0
4 | 6 | 203.04 | 53.184 | 8.1 | 0
4 | 7 | 199.32 | 78.1793 | 0 | 0
4 | 8 | 209.808 | 46.2832 | 8.1 | 0
4 | 9 | 192.552 | 81.8426 | 0 | 0
4 | 10 | 209.808 | 54.1496 | 0 | 0
4 | 11 | 202.286 | 20.1713 | 0 | 0
4 | 12 | 200.054 | 43.4556 | 0 | 0
5 | 1 | 206.46 | 131.0674 | 0 | 0
5 | 2 | 173.9925 | 187.7113 | 11.34 | 0
5 | 3 | 193.9725 | 161.3043 | 11.34 | 0
5 | 4 | 199.8 | 182.1786 | 0 | 0
5 | 5 | 206.46 | 142.013 | 11.34 | 0
5 | 6 | 199.8 | 161.204 | 0 | 0
5 | 7 | 193.9725 | 193.7747 | 0 | 0
5 | 8 | 206.46 | 150.4463 | 11.34 | 0
5 | 9 | 199.8 | 175.7343 | 11.34 | 0
5 | 10 | 193.9725 | 195.6919 | 0 | 0
5 | 11 | 199.8 | 107.6473 | 11.34 | 0
5 | 12 | 193.9725 | 169.0571 | 11.34 | 0
6 | 1 | 190.827 | 160.4026 | 0 | 0
6 | 2 | 171.171 | 191.5636 | 11.34 | 0
6 | 3 | 203.112 | 141.7515 | 0 | 0
6 | 4 | 196.56 | 186.5306 | 11.34 | 0
6 | 5 | 190.827 | 171.3681 | 0 | 0
6 | 6 | 196.56 | 164.4507 | 0 | 0
6 | 7 | 190.827 | 197.9254 | 0 | 0
6 | 8 | 190.827 | 179.7085 | 11.34 | 0
6 | 9 | 184.275 | 204.9278 | 0 | 0
6 | 10 | 203.112 | 176.1111 | 0 | 0
6 | 11 | 196.56 | 113.4048 | 0 | 0
6 | 12 | 203.112 | 146.7498 | 11.34 | 0
7 | 1 | 187.6815 | 167.733 | 11.34 | 0
7 | 2 | 168.3495 | 195.4159 | 0 | 0
7 | 3 | 199.764 | 144.2034 | 11.34 | 0
7 | 4 | 193.32 | 191.9102 | 0 | 0
7 | 5 | 199.764 | 150.9532 | 11.34 | 0
7 | 6 | 193.32 | 167.6973 | 0 | 0
7 | 7 | 199.764 | 176.366 | 0 | 0
7 | 8 | 199.764 | 162.2835 | 0 | 0
7 | 9 | 181.2375 | 210.0614 | 11.34 | 0
7 | 10 | 187.6815 | 204.2451 | 11.34 | 0
7 | 11 | 181.2375 | 140.8431 | 11.34 | 0
7 | 12 | 199.764 | 150.6416 | 0 | 0
8 | 1 | 184.536 | 171.9807 | 0 | 0
8 | 2 | 165.528 | 198.2405 | 11.34 | 0
8 | 3 | 184.536 | 176.2733 | 11.34 | 0
8 | 4 | 178.2 | 221.7698 | 11.34 | 0
8 | 5 | 196.416 | 156.451 | 11.34 | 0
8 | 6 | 178.2 | 197.4792 | 11.34 | 0
8 | 7 | 184.536 | 206.2268 | 11.34 | 0
8 | 8 | 184.536 | 189.0854 | 11.34 | 0
8 | 9 | 178.2 | 213.1398 | 11.34 | 0
8 | 10 | 196.416 | 183.0141 | 11.34 | 0
8 | 11 | 178.2 | 143.9122 | 11.34 | 0
8 | 12 | 196.416 | 156.0939 | 0 | 0

## summary
year | Power Fulfilment Factor, % | Energy Fulfillment Factor, % | Energy Production, MWh | OPEX, M PKR | CO2 Emissions, MT | Equivalent Tariff, PKR/kWh
1 | 100 | 100 | 17997.7987 | 912.9465 | 3011.547 | 50.7255
2 | 100 | 100 | 18028.0448 | 999.5057 | 3018.0034 | 55.4417
3 | 100 | 100 | 18058.291 | 1126.017 | 3117.1858 | 62.3546
4 | 100 | 100 | 18088.5371 | 1230.0859 | 3076.3702 | 68.0036
5 | 100 | 100 | 24516.4023 | 1832.4664 | 4405.6729 | 74.7445
6 | 100 | 100 | 24546.6485 | 2004.0207 | 4398.0245 | 81.6413
7 | 100 | 100 | 24577.7199 | 2211.0737 | 4422.0412 | 89.9625
8 | 100 | 100 | 24614.0352 | 2479.9189 | 4532.7866 | 100.7522

## power_summary
year | month | hour | Prod Demand in MW | Cooling demand in TR | Free Cooling available in TR | BESS Charging Demand | Total power demand incl. Cooling & BESS in MW | Solar Output in MW | Solar Loading in % | Gas Generator Output in MW | Gas Generator Loading in % | Existing Gas Generators Output in MW | Existing Gas Generators Loading in % | Grid Output in MW | Grid Loading in % | Diesel Generator Output in MW | Diesel Generator Loading in % | Final Unserved Load
1 | 2 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.4775 | 100 | 0 | 0 | 4.3077 | 95.7261 | 0 | 0 | 0
2 | 1 | 8 | 5 | 900 | 790.965 | 0.375 | 5.4577 | 0.043296 | 100 | 1.455 | 100 | 1.8 | 100 | 2.1594 | 47.9862 | 0 | 0 | 0
3 | 9 | 3 | 5 | 900 | 778.9365 | 0.375 | 5.4668 | 0 | 0 | 1.4325 | 100 | 1.773 | 100 | 2.2613 | 50.251 | 0 | 0 | 0
4 | 3 | 19 | 5 | 900 | 766.908 | 0.375 | 5.4759 | 0.001936 | 100 | 1.41 | 100 | 1.746 | 100 | 2.318 | 51.5106 | 0 | 0 | 0
5 | 7 | 12 | 7 | 900 | 754.8795 | 0.375 | 7.485 | 0.9888 | 100 | 1.3875 | 100 | 1.719 | 100 | 3.3897 | 75.3274 | 0 | 0 | 0
6 | 6 | 24 | 7 | 900 | 742.851 | 0.375 | 7.4942 | 0 | 0 | 1.365 | 100 | 1.692 | 100 | 4.4372 | 98.6034 | 0 | 0 | 0
7 | 7 | 19 | 7 | 900 | 730.8225 | 0.375 | 7.5033 | 0.054752 | 100 | 1.3425 | 100 | 1.665 | 100 | 4.441 | 98.6894 | 0 | 0 | 0
8 | 9 | 1 | 7 | 900 | 718.794 | 0.375 | 7.5124 | 0 | 0 | 1.32 | 100 | 1.638 | 100 | 4.5 | 100 | 0.054394 | 2.3983 | 0

## energy_summary
year | Prod Energy Req, MWh | Cooling Energy Req, MWh | Cooling Energy Req after CHP adj., MWh | BESS Charging Energy Req, MWh | Total Energy Req, MWh | Solar Output in MWh | Remaining Energy Demand (after Renewables) MWh | Gas Generator Potential Failures | Gas Generator Failures mitigated | Gas Generator Unavailability, hrs | Gas Generator Output in MWh | Existing Gas Generators Potential Failures | Existing Gas Generators Failures mitigated | Existing Gas Generators Unavailability, hrs | Existing Gas Generators Output in MWh | Grid Potential Failures | Grid Failures mitigated | Grid Unavailability, hrs | Grid Peak Energy, MWh | Grid Off Peak Energy, MWh | Diesel Generator Output in MWh | Final Unserved Energy Req in MWh
1 | 15994.0476 | 4264.365 | 1915.251 | 88.5 | 17997.7987 | 3513.664 | 14484.1347 | 5 | 5 | 0 | 12547.3356 | 6 | 6 | 0 | 0 | 45 | 45 | 0 | 422.3171 | 1874.4819 | 95.42 | 0
2 | 15994.0476 | 4264.365 | 1945.4972 | 88.5 | 18028.0448 | 3485.328 | 14542.7168 | 6 | 6 | 0 | 12308.3343 | 3 | 3 | 0 | 2504.3825 | 40 | 40 | 0 | 8.1148 | 36.8852 | 0 | 0
3 | 15994.0476 | 4264.365 | 1975.7433 | 88.5 | 18058.291 | 3456.992 | 14601.299 | 9 | 9 | 0 | 11968.5375 | 10 | 10 | 0 | 3037.7615 | 39 | 39 | 0 | 24.5972 | 110.4028 | 0 | 0
4 | 15994.0476 | 4264.365 | 2005.9895 | 88.5 | 18088.5371 | 3428.656 | 14659.8811 | 8 | 8 | 0 | 11844 | 5 | 5 | 0 | 3175.8811 | 41 | 41 | 0 | 25.6709 | 109.3291 | 0 | 0
5 | 22391.6667 | 4264.365 | 2036.2356 | 88.5 | 24516.4023 | 3400.32 | 21116.0823 | 5 | 5 | 0 | 11842.3125 | 7 | 7 | 0 | 9588.7698 | 39 | 39 | 0 | 81.7345 | 359.2655 | 0 | 0
6 | 22391.6667 | 4264.365 | 2066.4818 | 88.5 | 24546.6485 | 3371.984 | 21174.6645 | 6 | 6 | 0 | 11588.85 | 4 | 4 | 0 | 9963.8145 | 41 | 41 | 0 | 46.5125 | 205.4875 | 0 | 0
7 | 22391.6667 | 4264.365 | 2097.5532 | 88.5 | 24577.7199 | 3343.648 | 21234.0719 | 5 | 5 | 0 | 11458.2375 | 6 | 6 | 0 | 10090.8344 | 43 | 43 | 0 | 70.6474 | 307.3526 | 0 | 0
8 | 22391.6667 | 4264.365 | 2133.8685 | 88.5 | 24614.0352 | 3315.312 | 21298.7232 | 9 | 9 | 0 | 11028.6 | 10 | 10 | 0 | 10837.1232 | 45 | 45 | 0 | 114.8557 | 515.1443 | 0 | 0

## energy_summary_concise
year | Total Energy Req, MWh | Solar Output in MWh | Gas Generator Output in MWh | Existing Gas Generators Output in MWh | Grid Peak Energy, MWh | Grid Off Peak Energy, MWh | Diesel Generator Output in MWh | Final Unserved Energy Req in MWh
1 | 17997.7987 | 3513.664 | 12547.3356 | 0 | 422.3171 | 1874.4819 | 95.42 | 0
2 | 18028.0448 | 3485.328 | 12308.3343 | 2504.3825 | 8.1148 | 36.8852 | 0 | 0
3 | 18058.291 | 3456.992 | 11968.5375 | 3037.7615 | 24.5972 | 110.4028 | 0 | 0
4 | 18088.5371 | 3428.656 | 11844 | 3175.8811 | 25.6709 | 109.3291 | 0 | 0
5 | 24516.4023 | 3400.32 | 11842.3125 | 9588.7698 | 81.7345 | 359.2655 | 0 | 0
6 | 24546.6485 | 3371.984 | 11588.85 | 9963.8145 | 46.5125 | 205.4875 | 0 | 0
7 | 24577.7199 | 3343.648 | 11458.2375 | 10090.8344 | 70.6474 | 307.3526 | 0 | 0
8 | 24614.0352 | 3315.312 | 11028.6 | 10837.1232 | 114.8557 | 515.1443 | 0 | 0

## emissions_summary
year | CO2 Emissions from Gas Generator, MT | CO2 Emissions from Existing Gas Generators, MT | CO2 Emissions from Grid, MT | CO2 Emissions from Diesel Generator, MT
1 | 2550.4131 | 0 | 413.4238 | 47.71
2 | 2495.8149 | 514.0885 | 8.1 | 0
3 | 2477.9935 | 614.8923 | 24.3 | 0
4 | 2405.884 | 646.1862 | 24.3 | 0
5 | 2368.4625 | 1957.8304 | 79.38 | 0
6 | 2317.77 | 2034.8945 | 45.36 | 0
7 | 2291.6475 | 2062.3537 | 68.04 | 0
8 | 2205.72 | 2213.6666 | 113.4 | 0

## opex_summary
year | Solar Depreciation Cost, M PKR | Solar Fixed Opex, M PKR | BESS Depreciation Cost, M PKR | BESS Fixed Opex, M PKR | Gas Generator Depreciation Cost, M PKR | Gas Generator Fixed Opex, M PKR | Gas Generator Var OPEX, M PKR | Fuel Charges for RLNG, M PKR | Existing Gas Generators Depreciation Cost, M PKR | Existing Gas Generators Fixed Opex, M PKR | Existing Gas Generators Var OPEX, M PKR | Fuel Charges for NG, M PKR | Grid Fixed Opex, M PKR | Grid Peak Rate Energy Cost, M PKR | Grid Offpeak Rate Energy Cost, M PKR | Diesel Generator Depreciation Cost, M PKR | Diesel Generator Fixed Opex, M PKR | Diesel Generator Var OPEX, M PKR | Fuel Charges for Diesel, M PKR | Loss due to Interruptions, M PKR | Loss due to Outage, M PKR
1 | 4 | 4.62 | 18.15 | 7.92 | 2.0833 | 5.94 | 49.0955 | 659.2818 | 0 | 0 | 0 | 0 | 27.324 | 23.9661 | 94.4158 | 5.94 | 2.376 | 0.15744 | 7.6766 | 0 | 0
2 | 4 | 5.082 | 18.15 | 8.712 | 2.0833 | 6.534 | 52.8489 | 709.685 | 2.5 | 8.712 | 10.8858 | 129.1525 | 30.0564 | 0.50655 | 2.0437 | 5.94 | 2.6136 | 0 | 0 | 0 | 0
3 | 4 | 5.5902 | 18.15 | 9.5832 | 2.0833 | 7.1874 | 57.7187 | 775.0792 | 2.5 | 9.5832 | 14.3224 | 169.9248 | 33.062 | 1.689 | 6.7287 | 5.94 | 2.875 | 0 | 0 | 0 | 0
4 | 4 | 6.1492 | 18.15 | 10.5415 | 2.0833 | 7.9061 | 61.643 | 827.7769 | 2.5 | 10.5415 | 16.5564 | 196.4301 | 36.3682 | 1.939 | 7.3295 | 13.8461 | 6.3249 | 0 | 0 | 0 | 0
5 | 4 | 6.7641 | 18.15 | 11.5957 | 2.0833 | 8.6968 | 66.7526 | 896.3916 | 2.5 | 11.5957 | 55.1793 | 654.6635 | 40.0051 | 6.791 | 26.4941 | 13.8461 | 6.9574 | 0 | 0 | 0 | 0
6 | 4 | 7.4406 | 18.15 | 12.7552 | 2.0833 | 9.5664 | 71.8562 | 964.9267 | 2.5 | 12.7552 | 63.0864 | 748.4756 | 44.0056 | 4.251 | 16.6691 | 13.8461 | 7.6531 | 0 | 0 | 0 | 0
7 | 4 | 8.1846 | 18.15 | 14.0308 | 2.0833 | 10.5231 | 78.151 | 1049.4566 | 2.5 | 14.0308 | 70.3315 | 834.4332 | 48.4061 | 7.1025 | 27.4256 | 13.8461 | 8.4185 | 0 | 0 | 0 | 0
8 | 4 | 9.0031 | 18.15 | 15.4338 | 2.0833 | 11.5754 | 82.7427 | 1111.1168 | 2.5 | 15.4338 | 83.0408 | 985.2203 | 53.2467 | 12.7016 | 50.564 | 13.8461 | 9.2603 | 0 | 0 | 0 | 0

## opex_summary_concise
year | BESS Fixed Opex, M PKR | Gas Generator Fixed Opex, M PKR | Fuel Charges for RLNG, M PKR | Existing Gas Generators Fixed Opex, M PKR | Fuel Charges for NG, M PKR | Loss due to Interruptions, M PKR | Loss due to Outage, M PKR | Source Depreciation, M PKR | Renewable OPEX, M PKR | Power Plant OPEX, M PKR | Diesel OPEX, M PKR | Grid OPEX, M PKR | PPA OPEX, M PKR
1 | 7.92 | 5.94 | 659.2818 | 0 | 0 | 0 | 0 | 30.1733 | 4.62 | 49.0955 | 10.2101 | 145.7059 | 0
2 | 8.712 | 6.534 | 709.685 | 8.712 | 129.1525 | 0 | 0 | 32.6733 | 5.082 | 63.7347 | 2.6136 | 32.6066 | 0
3 | 9.5832 | 7.1874 | 775.0792 | 9.5832 | 169.9248 | 0 | 0 | 32.6733 | 5.5902 | 72.041 | 2.875 | 41.4797 | 0
4 | 10.5415 | 7.9061 | 827.7769 | 10.5415 | 196.4301 | 0 | 0 | 40.5795 | 6.1492 | 78.1994 | 6.3249 | 45.6368 | 0
5 | 11.5957 | 8.6968 | 896.3916 | 11.5957 | 654.6635 | 0 | 0 | 40.5795 | 6.7641 | 121.9319 | 6.9574 | 73.2902 | 0
6 | 12.7552 | 9.5664 | 964.9267 | 12.7552 | 748.4756 | 0 | 0 | 40.5795 | 7.4406 | 134.9427 | 7.6531 | 64.9257 | 0
7 | 14.0308 | 10.5231 | 1049.4566 | 14.0308 | 834.4332 | 0 | 0 | 40.5795 | 8.1846 | 148.4825 | 8.4185 | 82.9342 | 0
8 | 15.4338 | 11.5754 | 1111.1168 | 15.4338 | 985.2203 | 0 | 0 | 40.5795 | 9.0031 | 165.7836 | 9.2603 | 116.5123 | 0