## Sheet1
No. | Scenario Description | Energy Fulfillment Ratio | Critical Load Interruptions | Avg Unit Cost (PKR/ kWh) | Notes
1 | Status Quo: 5MW PV plant with 9 x 1.5MW HSD GS | 100 | 0 | 114.3 | Spin Reserve = 10%
2 | 5MW PV plant, with 4 x 2.5MW HFO GS, starting from Year 1 | 99.99 | 0 | 86.9 | Starting in Year 1 may not be realistic due to lead time
3 | 5MW PV plant, with 6 x 1.5MW HSD sets for Year1. 4 x 2.5MW HFO GS start from Year 2 | 99.99 | 0 | 89.13 | Perhaps a more practical version of '2'
4 | 5MW + 10MW (from year 2) PV Plant, 4 x 1.5MW HSD GS, 3 MW BESS (Year 2) | 72 | 2 | 100 | 15MW Solar creates excessive capacity during night time. 4 x 1.5MW cannot meet night load, esp in later years.)
5 | 5MW PV Plant with 10MW ST added in Year 3, 6 x 1.5MW HSD continue till Year 2. | 100 | 4 | 72.49 | Excellent economy, but does face longer term black-out risk if ST fails
6 | 5MW PV Plant with 10MW ST added in Year 3, 4 x 1.5MW HSD continue till Year 2. | 99.78 | 2 | 72.11
7 | 5MW + 5MW (from year 2) PV plant + 4 x 1.5MW HSD (till Year 1), 4x2.5 MW HFO GS from year 2 | 99.9 | 12 | 83.93
8 | 5MW PV plant, with 4 x 1.5MW HSD sets. 4 x 10MW ST start from Year 3 | 99.8 | 4 | 73.105 | A more practical variant of 5 and 6.